## Slide 1: Equipment Installation Last Update 2013.05.15
1.37.0

## Slide 2: Objectives of This Section
Learn how to
  Setup a site the proper way by conforming to generally accepted standards and regulations
  Use common techniques and guidelines related to equipment installation

## Slide 3: Standards
The TIA-942 standard along with the other structured cabling standards provide a guide to the setup of a data center

## Slide 4: Planning Steps
Ensure the equipment received can be moved into place
  Such as door widths, weight of equipment, security access
Check that any support needed, both internal and vendors, will be accessible when the work is being done
  Such as 2 AM Sunday morning

## Slide 5: Planning Steps
Have a rollback plan in place
  In other words have a retreat path that will take you back to where you were in case the installation does not work out

## Slide 6: What to Call the Places
The name used to describe where you put all of the stuff you need to run a network varies widely depending on who your talking to and the exact purpose of the particular room
It also depends on whether you are adhering strictly to the standards, as they call out specific names for specific rooms

## Slide 7: What to Call the Places
In many cases all of the individual rooms the standards call for do not exist

## Slide 8: What to Call the Places

## Slide 9: What to Call the Places
In practice one room does many functions
This is especially true in older buildings
Strictly speaking there are two main types of equipment rooms
  Main
  Intermediate

## Slide 10: What to Call the Places
The main room, often called the MDF - Main Distribution Frame room by telco people, is where the bulk of the equipment resides
Another type of room, IDF - Intermediate Distribution Frame in telco talk, is where devices are placed when the distance is too far or the site is too large for everything to go in the MDF

## Slide 11: What to Call the Places
Many LAN folks call the MDF the LAN or server room
They will refer to the IDFs as IDFs in most cases.

## Slide 12: LAN Room Names
LAN rooms go by many names
  LAN room
  Server room
  Equipment room
  Wiring closet
  Telecommunications closet
  Telecommunications room
  MDF - Main distribution frame
  IDF -Intermediate distribution frame

## Slide 13: LAN Room Names
  MCC – Main cross-connect
  ICC – Intermediate cross-connect

## Slide 14: What Not to Do
The first thing about an equipment room is that it should be a room of some sort
Security is always important so I would never just leave equipment out in an open area as the next slide shows
Yes this is a site I provide support for
I have been over this with them several times, but they trust everybody
Yeah, right

## Slide 15: What Not to Do

## Slide 16: Design Specifications
The standard calls for these specifications for the telecommunications room or closet
  This room should only be used for telecommunications functions
  Equipment not related to telecommunications shall not be installed, pass through or enter the telecommunications room
  Multiple closets on the same floor shall be interconnected by a minimum of one 78mm conduit, or equivalent pathway

## Slide 17: Design Specifications
  Minimum one closet per floor to house telecommunications equipment and cable terminations and associated cross-connect cable and wire
  Located near the center of the area being served.
  Horizontal pathways shall terminate in the telecommunications room on the same floor as the area served

## Slide 18: Design Specifications
  One wall should have 20mm (0.75 in.) A-C plywood 2.4m (8 ft.) high
  Lighting shall be a minimum of 500 lx (50 foot candles) at 1m (3 ft.) above finished floor (AFF)
  False ceilings shall not be provided
  Minimum door size 910mm (36 in.) wide and 2000mm (80 in.) high without sill, hinged to open outwards, or slide side-to-side or removable, and fitted with a lock

## Slide 19: Design Specifications
  Minimum of two dedicated 120V nominal non-switched duplex electrical outlet receptacles or equivalent, each on separate branch circuits
  Additional convenience duplex outlets placed at 1.8m (6 ft.) intervals around perimeter, 150mm (6 in.) above floor
  Access to the telecommunications grounding system as specified by ANSI-J-STD-607-A

## Slide 20: Design Specifications
  HVAC requirements to maintain temperature the same as adjacent office area
  A positive pressure shall be maintained with a minimum of one air change per hour or per code

## Slide 21: Design Specifications

## Slide 22: Small Size Room
The room does not even need to be a room
It can be a locked and ventilated or air conditioned cabinet in an otherwise open area
At a small site there is no need for a separate room
These typically cost from $1,000 to $3,000

## Slide 23: Equipment Cabinet

## Slide 24: Medium Size Room
A medium size equipment room is typically about the size of an office and it may be a spare office

## Slide 25: Large Size Room
A large equipment room is anything larger than a standard size office
It may just be a large room
If it gets large enough it may be more specialized as seen here

## Slide 26: Large Room

## Slide 27: Raised Floor
Often these larger rooms will have a raised floor
This type of floor is used to route cabling
There are several different types of raised floors
The best currently available uses a composite panel for the floor tile
This is a composite wood product covered in steel

## Slide 28: Raised Floor
These panels are supported by stands placed directly on the concrete floor
Cost for a floor like this runs from $10 to $20 per square foot of floor area

## Slide 29: Raised Floor

## Slide 30: Raised Floor

## Slide 31: Raised Floor

## Slide 32: Raised Floor Layout

## Slide 33: Overhead Cable Racks

## Slide 34: Overhead Cable Racks

## Slide 35: Raised Floor v Overhead Rack
Over the last few years opinion has coalesced around the idea that power cables should go under the raised floor and the data cables overhead in basket racks

## Slide 36: Sensors
Equipment rooms need to be monitored for problems that occur when no one is around
These often include sensors for
  Heat
  Water
  Humidity
  Airflow around equipment
  Door open

## Slide 37: Sensors
  Power outage
  Hydrogen alarm for battery backup

## Slide 38: Sensors
Some of these also include audio, to listen for strange equipment sounds, and a camera to see who is in the room
A good example of an integrated unit doing this are the two from NetBotz
  The WallBotz is a web-accessed, environment-monitoring appliance in a book-sized package

## Slide 39: Sensors
  As the manufacturer says
    Completely self-contained, the unit continually checks the room environment, including temperature, humidity, smoke, and airflow
    Alarms are sent via email and pager when a connected device's environment condition is out of range
    A built-in camera records individuals accessing the server room and allows both the customer and technician to easily view the condition of equipment via an internally generated web page

## Slide 40: Sensors
  The RackBotz is a web-accessed, environment-monitoring appliance
  As the manufacturer says
    Alarms providing you with advanced warning of equipment failure are sent via email and pager when a connected devices condition is out of range
    A built-in camera records individuals accessing the rack or cabinet and allows both the customer and technician to easily view the condition of equipment via an internally generated web page
These range in price from $800 to $1,000

## Slide 41: Heat Sensor

## Slide 42: Heat Load
Depending on the room size and the equipment in the room a separate air conditioner may be needed
These can be in room or placed in the space above the ceiling tiles
Equipment manufacturers will have heat load figures for their equipment
If not most HVAC companies have standardized figures

## Slide 43: APC Heat Load Computation
Here is what APC had to say on this
  To ensure continuous operation of the equipment in the wiring closet 7 x 24 x 365, cooling and airflow issues must be identified and addressed
  Power dissipation in the wiring closet should be calculated to decide on a cost effective method to solve the problem

## Slide 44: APC Heat Load Computation
  The most important thing to note here is that many network switches have a high power draw; however this does not mean that all the power is dissipated as heat inside the wiring closet
  For example a layer 2/3 switch may draw 1800W of power but it may be dissipating only 300-500W in the closet

## Slide 45: Heat Load Computation
  The rest of power is supplied over the network to the various devices like wireless access points, IP phones, security cameras scattered and is dissipated throughout the office area

## Slide 46: APC Heat Load Table 1

## Slide 47: APC Heat Load Table 2 - Part

## Slide 48: APC Heat Load Table 2 - Part

## Slide 49: Heat Load Guidelines
APC has some guidelines for determining how to cool equipment closets in White Paper #68 from 2007
The next few slides are from this white paper
According to APC the typical recommended operating temperatures from IT equipment vendors are between 70°F (21°C) and 75°F (24°C)

## Slide 50: Heat Load Guidelines
In addition, The American Society of Heating, Refrigeration, and Air Conditioning Engineers (ASHRAE) TC 9.9 publishes both recommended and allowable operating temperatures for IT equipment

## Slide 51: Heat Load Guidelines

## Slide 52: Heat Load Guidelines
  The goal should always be to maintain temperatures no higher than 77°F (25°C)
  However, if doing so is not possible, maintaining below the maximum allowable temperature of 90°F (32°C) can be a suitable solution for less critical closets
  Any temperature above 90°F (32°C) should be avoided to reduce risk of equipment failure

## Slide 53: Heat Load Guidelines
  Also, 90°F (32°C) is the maximum temperature organizations such as the Occupational Safety and Health Administration (OSHA) and International Organization for Standardization (ISO) deem permissible for light work loads
  More careful consideration must be given to closet environments where a UPS is deployed

## Slide 54: Heat Load Guidelines
  Increases in temperature have a much more pronounced effect on battery longevity than other types of IT equipment
  A user can expect a typical UPS battery operating at 104°F (40°C) to only last 1.5 years or less as compared to the usual 3 – 5 years at normal operating conditions
  An operating temperature below 77°F (25°C) should be a requirement

## Slide 55: Heat Load Guidelines
Heat can leave a small confined space like an office or closet in four different ways
  Conduction
    Heat can flow through the walls of the space
  Ventilation
    Heat can flow into cooler air via a vent or grille, without an air moving device
    Heat can flow into cooler air via a vent or grille that has an air moving device

## Slide 56: Heat Load Guidelines
  Building Cooling
    Heat can be removed by a building’s comfort cooling system
  Dedicated Cooling
    Heat can be removed by a dedicated air conditioner

## Slide 58: Conduction
When using conduction heat can flow through the walls of the space
If a closet is effectively sealed, then the only way for the heat to leave is by conduction through the walls
For this to work, the air in the closet must heat up to the point where it is hotter than the temperature that is on the other side of the closet walls

## Slide 59: Conduction
Practically, this means that the closet will always be hotter than the other ambient air within the building, and the degree of temperature rise will be greater as the power level of the IT equipment increases
The size of the room, as well as the material the walls and so forth are made of affect this

## Slide 60: Conduction
One common occurrence that impacts conductive cooling performance is a rise in the building ambient air temperature, due to weekend cooling setbacks
When this happens, the closet temperature will rise in step

## Slide 61: Conduction
Another limitation of this method of cooling is that if one of the closet walls is an outside wall of the building, the closet temperature will be subject to the outdoor wall temperature, which is effected by both the ambient outdoor temperature and the heating due to sun exposure

## Slide 62: When to Use Conduction
Use conduction as a sole means of cooling for critical closets when the power load within the closet is less than 400 watts with consideration given to other factors as mentioned above that will impact cooling performance
For non-critical closets, conduction should only be used when the load in the closet is less than 1000 W

## Slide 63: Ventilated Closet
Closets can be cooled by venting them to the ambient building air
The venting can be passive using appropriately placed holes or vents, or it may be fan-assisted
The basic principle is to ensure that the closet air temperature does not rise substantially above the building ambient air temperature

## Slide 64: Vented Closet

## Slide 65: When to Use Ventilation
For power levels below 700 watts, passive ventilation is effective for critical closets
For power levels of between 700 watts and 2000 watts, fan-assisted ventilation is appropriate for critical closets
Support of even higher power levels can be achieved if higher capacity or multiple fan assist units are used

## Slide 66: When to Use Ventilation
Likewise, for non-critical closets, passive ventilation is effective for up to 1750 watts, and fan-assisted ventilation is effective from 1750 watts to 4500 watts

## Slide 67: Using Building Cooling
This is generally a bad idea
Building cooling systems cycle on and off
A thermostat placed somewhere in the zone, but not in the closet is the usual control mechanism
For a small space like a closet with IT devices, this means that the temperature will decrease when the cooling system is on, and increase when it is off

## Slide 68: Using Building Cooling
This results in significant swings in temperature that actually stress IT equipment more than sustained higher temperature conditions
Furthermore, best practice for comfort cooling systems involves turning up the temperature set points on week nights and weekends to help conserve electricity
Some are actually shut off completely

## Slide 69: Using Building Cooling
If a wiring closet is part of a larger zone, the average temperature of the wiring closet will increase by the amount the temperature set point is increased
By simply adding ductwork, one is forced to choose between wasting electricity on nights and weekends and making the temperature swings in the wiring closet even worse

## Slide 70: Using Building Cooling
In order to use a building comfort cooling system to cool a wiring closet, the wiring closet in question would have to be made into a dedicated zone with its own properly sized supply and return ducts, terminal units, and controls
This is not practical

## Slide 71: Dedicated Cooling
The most effective way to gain control of closet temperatures is by installing dedicated closet air conditioning equipment
In general, when the power level in a closet exceeds approximately 2000 W for critical closets or 4500 W non-critical closets, dedicated air conditioning equipment is recommended

## Slide 72: In Room AC Unit

## Slide 73: Ceiling AC Unit

## Slide 74: Wall Mount AC Unit

## Slide 75: Portable AC Unit

## Slide 76: Air Flow Options

## Slide 77: Air Flow Options

## Slide 78: UPS Impact on Cooling
When a UPS is installed, the IT equipment will continue to create heat during a power outage
Therefore the cooling system must continue to operate
If the backup time is less than 10 minutes, the thermal mass of the air and wall surfaces within the closet will keep the temperature within reasonable limits

## Slide 79: UPS Impact on Cooling
However, if the UPS is designed to provide runtime in excess of 10 minutes the cooling system must continue to operate during this period

## Slide 80: Liquid Cooling
As data centers switch from standalone servers in separate cases to chassis with blade servers heat will become even more of a problem
Some think liquid cooling of the servers is the answer
If so, this will introduce a whole new level of complication to the data center

## Slide 81: Water Protection
Water always rises
However, it may arrive at the site from any number of directions
For example, read what happened to these poor folks

## Slide 82: Water Protection
TESSCO’s Disaster Recovery Continues
  On Saturday night our entire central voice, data, and e-commerce technology center was destroyed!
  Let me recap what happened, last Saturday evening, October 12 2002, a malfunctioning public water system resulted in a 6-inch main driving water with tremendous force directly toward the outside wall of TESSCO’s Global Logistics Center in Hunt Valley

## Slide 83: Water Protection
  The “water cannon” blew a three-foot square hole through the wall, immediately into our network operating center, destroying the equipment and functionality of our central voice, data, and Internet systems

## Slide 84: The Water Cannon At Work

## Slide 85: The Result

## Slide 86: More Results

## Slide 87: Other Causes
Other causes of water in an equipment room include
  Windows blown out by a storm
  Roof leaks
  Fire suppression sprinkler system leaks
  Firefighting efforts on floors above you can cause water to end up in your area

## Slide 88: Water Protection
So what do you do
There is no good answer
Some ideas that have been tried include
  For rising water
    Floor drains
    Sump pumps
    Wet/Dry vacuums

## Slide 89: Water Protection
  For falling water
    Rolled-up plastic tarps on rollers suspended from the ceiling, with a good solid handle dangling down on a rope
Also
  Consider putting data centers not on the ground floor or the basement,
  Mount equipment 18” off the floor

## Slide 90: Fire Protection
Computer equipment does not like being sprayed with water
A better solution for fire protection is a system designed to suppress fire without unduly damaging the equipment
If local codes allow, be sure the sprinkler heads in the equipment room are disabled

## Slide 91: Fire Protection
Fire suppression systems are not cheap
From design through installation the cost will be around $30,000 in year 2000 dollars
Such a system also requires space for the extinguisher storage bottles

## Slide 92: Fire Protection
A common system uses a pressurized gas called FM200
Chemically known as heptafluoropropane
It is also known as HFC-27ea
It is a replacement for the ozone depleting Halon 1301 used extensively before 1994

## Slide 93: Fire Protection

## Slide 94: Fire Protection

## Slide 95: Fire Protection

## Slide 96: Fire Protection

## Slide 97: Computer Hardware Storage
Once you have a room setup, where do you put all of this stuff
Let’s look at some options
But first, don’t do it this way

## Slide 98: How Not To Do This

## Slide 99: Relay Rack
The easiest way to keep things straight is to place the equipment and devices in a rack
The most common type is called a Relay Rack
In the picture in a few slides the extra length on the patch cables is hidden inside the cable management system on the left side of the Relay Rack

## Slide 100: Relay Rack
The cables can be seen on the right side where the cable management cover has been removed
This unit is about seven feet tall and two feet wide
It is attached to the concrete floor with bolts and braced to the wall
Equipment is attached to the rack with machine screws

## Slide 101: Relay Rack

## Slide 102: Relay Rack

## Slide 103: Relay Rack

## Slide 104: Relay Rack
Be sure the Relay Rack itself is grounded to a suitable building ground
In addition to the rack the joints between all the various parts of the structure, such as the supporting ladder racks, must be connected to each other with short ground straps
This is especially true for painted components

## Slide 105: Grounding Racks

## Slide 106: Grounding Racks

## Slide 107: Grounding Racks

## Slide 108: Grounding Racks

## Slide 109: Grounding Racks

## Slide 110: Grounding Racks

## Slide 111: Grounding
The standards call for a two-hole compression lug for the attachment to the ground bar
The wire used should have a green color to indicate its use as a grounding connection
In general a #6 AWG wire will suffice for these types of short runs

## Slide 112: Grounding
Although not yet a requirement it is expected that the standard will eventually call for a jumper connection from all devices to the rack, instead of relying on the AC power cord ground wire
Other changes are expected as well

## Slide 113: Relay Rack
Things are mounted to a relay rack using Pan Head Machine Screws
  Of course any head style will work
The size is either a 10-32 or a 12-24 depending on the rack
  This refers to the diameter and thread pitch
They are ½” to ¾” long

## Slide 114: Relay Rack

## Slide 115: Relay Rack

## Slide 116: Relay Rack
Width of the rack is usually 19 inches
Some racks are 23 inches wide, especially those used with high price WAN equipment
Check the size of the equipment before having the rack installed

## Slide 117: Relay Rack
It is a good idea to document the layout of the boards in the hubs and other configuration information
A copy of the manuals, especially the quick setup manual, should be stored here also
These can be stored on the Relay Rack itself

## Slide 118: Relay Rack

## Slide 119: Relay Rack – Wall Mount
Relay racks need not be seven feet tall and bolted to the floor
They can be any size
If they are shorter than seven feet, then they are usually bolted to a wall and swing out for access

## Slide 120: Relay Rack – Wall Mount

## Slide 121: Equipment Rack
Instead of bolting something to the floor a free standing rack such as shown next may be used instead
It makes no difference, suit yourself
A rack like this costs from $2,000 to $4,000

## Slide 122: Equipment Rack

## Slide 123: Command Center
If you want to look really slick, spend money on a command center
Sitting at one of these you will think you know what you are doing, even if you don’t

## Slide 124: Command Center

## Slide 125: Equipment Cabinet
As mentioned above a room is not even needed if all of the equipment can be put into a single enclosed and ventilated enclosure
Equipment cabinets are also useful when installed in a large room with a raised floor
For example

## Slide 126: Equipment Cabinets

## Slide 127: Equipment Cabinet Front

## Slide 128: Equipment Cabinet Front

## Slide 129: Equipment Cabinet Back

## Slide 130: Equipment Cabinet
Be sure that the equipment will fit in the space available
Also account for the heat load that will go in the cabinet
Most equipment cabinets are rated to handle 3,000 to 5,000 BTUs

## Slide 131: Equipment Cabinet
The manufacturers of the stuff you are putting in the cabinet can supply BTU figures
If the heat load is too high, additional fans must be installed in the cabinet
Place the cabinet so that there is easy access to all doors, front, back or side
3 feet is good, if space is available

## Slide 132: The U
Things that mount in a relay rack or equipment cabinet are measured in rack units
One unit or 1U is 1.75”
So if the vendor says something is 7Us you know it will take up 12.25 inches of space
Standard size racks and cabinets hold 42 to 45Us of equipment

## Slide 133: Mounting Equipment
When equipment is mounted in a rack, put the heaviest stuff at the bottom, especially in a relay rack
The heaviest equipment is usually the UPS
Put the monitor where it can be seen
Put the keyboard where it can be used

## Slide 134: Bread Rack
All of the above is pretty expensive
Almost as good and much cheaper is a bread rack
Such as

## Slide 135: Bread Rack

## Slide 136: Bread Rack

## Slide 137: Crash Cart
If you really need to, you can put it all on wheels
This works especially well in test centers and for large diagnostic setups

## Slide 138: Crash Cart

## Slide 139: A Bunch of Tables
A less costly solution is to just put a bunch of tables in the room and stack everything on the them

## Slide 140: A Bunch of Tables

## Slide 141: The Wall
If there are only a couple of pieces of equipment, such as makes up this very small LAN, mount all of it to a wall

## Slide 142: The Wall

## Slide 143: The Floor
Finally if all else fails or you want to take a chance of water damage, crud, and people kicking the equipment, just put it on the floor
Although I do not recommend this idea

## Slide 144: The Floor

## Slide 145: KVM
To reduce the amount of equipment that has to be put in the rack or on the table a KVM – Keyboard, Video, Monitor – switch can be used
With such a thing a single keyboard, a single monitor, and a single mouse can be used to control from 2 to 200 computers
These look like this

## Slide 146: KVM

## Slide 147: KVM

## Slide 148: Headless Server
A server can also be managed remotely without a keyboard, monitor, or mouse being attached to it at all
This is done using Telnet or some other remote management program
This is called a headless server

## Slide 149: Electrical Power
Has anyone ever heard of any problems with the power supply anywhere in the country
Can anyone think of any reason to monitor, filter, or provide temporary power to computer equipment

## Slide 150: West Coast

## Slide 151: East Coast

## Slide 152: Electrical Power Management
There are several aspects to providing electrical power to the equipment room
These range from the proper installation of the power, to monitoring the quality of the power, and to what to do if the power goes off
Each of these will be discussed

## Slide 153: Power Supply
The first thing to do is be certain proper quality power is supplied to the WAN room
This is done when the room is first setup
The proper way to supply standard 120-volt power to a network device is through a dedicated, isolated, and grounded circuit
This means each circuit goes from its own breaker in the breaker panel to a single duplex outlet

## Slide 154: Power Supply
The only loads on this circuit are the ones attached to that outlet or to a power strip attached to that outlet
This prevents the problem of people plugging strip heaters into the same circuit, which then trip the breaker, resulting in the power going off

## Slide 155: Power Supply
This also prevents voltage variations from other equipment on the circuit going on, going off, or drawing various levels of power as it operates, such as a copy machine
Each circuit should also have an isolated ground which is one that is attached directly from the outlet to the circuit breaker panel

## Slide 156: Power Supply
For regular outlets the ground is via the conduit the cable is carried in or shared by other outlets through a common wire
The ground for these regular circuits may not be at the circuit breaker box, but to the building structure near the outlet

## Slide 157: Power Supply
This helps to be certain that quality power is delivered to each device
This type of circuit is designated by an orange outlet with a small green triangle

## Slide 158: Isolated Grounded Outlet

## Slide 159: NEMA L Series and Others
In many cases the electrical outlet will not use the common household type connector as shown above
Instead it will be something along these lines

## Slide 160: Electrical Connectors

## Slide 161: NEMA L Series and Others
These are discussed below in more detail

## Slide 162: Power Conditioning
Next is circuit protection and conditioning
This is done with surge protectors and circuit conditioners
The surge protector can be installed at the breaker box for the entire building, as part of a power strip, or built into the UPS
Circuit conditioning is usually part of the UPS in small to medium sized rooms

## Slide 163: Power Monitoring
The second thing to do is to monitor the power being supplied to the site
This is done using a power monitoring device such as those offered by PowerTronics at www.powertronics.com or Fluke at www.fluke.com

## Slide 164: Temporary Power
The last thing is to provide for temporary power if the main power fails
This can be done in three ways, each providing a step up in running time and cost

## Slide 165: Planning for Power Loss
There are four basic steps to planning for a power loss
  Determine the worst case scenario
    Are you concerned about a sag, spike, lightening, or other short term outage
    Or are you concerned about an extended outage due to failure of the power grid
  Decide what systems must be kept running and for how long
    As always compute if it is simply less expensive to suffer the downtime, than to correct it

## Slide 166: Planning for Power Loss
    In some cases, such as a hospital, it does not matter what the cost is
Count the kilowatts needed
  The number of these depends on the size of the organization and the equipment used
  There are some guidelines below
Decide whether to buy or rent
  Compute the costs for all alternatives
  Decide whether you want to hire or train someone to manage such a system

## Slide 167: Size the Power Supply
Regardless of the method used to provide the backup power be sure to size it according to the loads that will be placed on it
Depending on the size and cost of the site it may be best to have a power audit done by an electrical engineer or a company like APC - American Power Conversion, that makes UPSs

## Slide 168: Size the Power Supply
It will evaluate exactly what you have, what you need, and what needs to be done to get the site up to the required level for a few hundred to a few thousand dollars
For a basic estimate of the proper size UPS, which is the minimum power backup system everyone should have, a calculation of the VA - volt-amperes must be done

## Slide 169: Size the Power Supply
The problem is for older equipment power ratings are in watts and UPS ratings are in volt-amperes
Both of these measure power, but they are not the same thing
For the older equipment a power factor correction must be applied

## Slide 170: Size the Power Supply
You must make sure that the total VA used by your computer equipment is less than the VA available from the backup power system
Alternatively, you must make sure that the wattage used by your equipment is less than the wattage available from the backup power system

## Slide 171: Size the Power Supply
Only when all of your equipment has power factor correction can you indiscriminately mix the VA and watts in making comparisons
To convert a VA rating to a watt rating, multiply the VA by the power factor of the backup power supply

## Slide 172: Size the Power Supply
To go the other way, watts to VA, divide the wattage rating of the backup power system by its power factor
For computers made before the year 2000, a safe value to assume for the power factor is 2/3

## Slide 173: Size the Power Supply
If all you have is recently manufactured computers and peripherals, you need not worry about these details
Nearly all servers made since early in the year 2000 have built-in power factor correction, which means that the number of watts the equipment consumes equals the number of volt-amperes it consumes

## Slide 174: Size the Power Supply
Total up all the equipment you want to protect, and select a UPS that will handle it
The basic rule of thumb to use is
  If you do not know the VA loading, take the Watt rating of your equipment at 120 volts AC and multiply by 2.5 to figure a very safe VA rating

## Slide 175: UPS
A UPS is an Uninterruptible Power Supply
In essence it is a collection of batteries that provides running time for critical components if the main power goes off
Most UPSs provide from 10 minutes to two hours of running time
Once the battery runs down there is no more power

## Slide 176: Small UPS
A small UPS suitable for a few devices

## Slide 177: Medium UPS

## Slide 178: Medium UPS

## Slide 179: Large UPS

## Slide 180: Large UPS

## Slide 181: Large UPS

## Slide 182: Large UPS

## Slide 183: Large UPS
Each of the batteries in this array weighs 450 pounds
It takes 345 for this facility, which is a large telecom business

## Slide 184: What Size UPS
A rule used for determining whether you need a small, medium, or large UPS is to add up the kVA for the equipment to be protected, then add 25%
The better way is to talk to an expert, especially when a medium to large one is needed

## Slide 185: Types of UPSs
There are three basic kinds of UPS
The standby UPS is the simplest and the cheapest
It only switches to battery power if there is an incident; as such the switchover may be too slow to prevent loss of data

## Slide 186: Types of UPSs
Line-interactive systems will actively fix sags and spikes in line voltage with power conditioning transformers; they'll only switch to battery power when the source reaches a certain threshold voltage

## Slide 187: Types of UPSs
The advantage of the line-interactive UPS is that the batteries are not constantly being used and therefore not constantly being drained; so they should be at full power when an incident does arise
The last type of UPS is the online UPS
These are the best sources of power protection since they constantly convert power

## Slide 188: Types of UPSs
They receive AC power from the utility source, convert it into battery DC, and then back in to AC in a constant 120V stream
When power fluctuations occur from the outside line, they never make it to equipment since all power is regulated internally in the UPS

## Slide 189: Types of UPSs
Because of this, the power that goes to the equipment is always cleaned - that is, there is no noise, because of the "double-conversion" process within the UPS
There is no transfer time between utility source and battery

## Slide 190: Types of UPSs
Online UPS' eliminate most noise and provide the steadiest voltage of the three different types and can usually protect against the most massive of spikes and surges compared to the others

## Slide 191: Batteries
Regardless of the size or type of UPS the batteries will eventually have to be replaced
This can be on a schedule or when the periodic tests you should also be doing show the need

## Slide 192: UPS Connectors
As the size of the UPS goes up the connectors used changes from the standard household plug
This is to ensure a solid connector
Prevent unplugging by accident
And ensuring proper grounding
An example of a common connector used is the NEMA L series

## Slide 193: UPS Connectors

## Slide 194: UPS Connectors

## Slide 195: UPS Connectors
To use these the wall outlet will have to be wired with the correct plug
The equipment that will connect to the UPS will also have to have the correct plug

## Slide 196: Automatic Shutdown
Keep in mind that even with a UPS when the batteries run down, there is no more power
The servers stop running
This is very bad on most servers
If the power loss occurs while everyone is at work, no problem, just go down the servers using the approved method

## Slide 197: Automatic Shutdown
What if the power goes off at 2 in the morning during a driving thunderstorm
The point being that a battery backup without a program running on the server that talks to the UPS is pointless
Who is going to go into work at two in the morning during a severe thunderstorm to turn off the server

## Slide 198: Automatic Shutdown
An automatic shutdown program will do this for you
This will help to save the data on the server

## Slide 199: Generator
If the site must continue in operation after the expected running time of a UPS, the next step up is a generator powered by a gasoline or diesel engine
The size depends on the load
A very small site might get by with one this size, which you can store in a closet

## Slide 200: Small Generator

## Slide 201: Large Generator
In most cases a site that needs to be kept running regardless of power loss is quite a large site
As such it will need a bigger generator
Like these

## Slide 202: Generator

## Slide 203: Generator

## Slide 204: Generator

## Slide 205: Generator
Size of Organization | 25 Person Office | 200 Room Hotel | 500 Person Office
Generator Capacity | 75 kW | 400 kW | 2,000 kW
Engine Type | Natural Gas/Diesel | Diesel | Diesel
Engine Size | 125 hp | 600 hp | 1,500 hp
Fuel for 48 hours | 100 gallons | 400 gallons | 1,320 gallons
Purchase Cost | 20,000 | 100,000 | 600,000
Rental Cost | 2,000 | 5,000 | 25,000

## Slide 206: Multiple Power Grids
The final level is to attach the site to two entirely different power grids if the electrical power provider can do this
This way if the main power grid fails, the electrical service will be switched to the second grid

## Slide 207: Fuel Cell
Instead of all of this some organizations are starting to use fuel cells instead
For example as the web site of one of the companies selling these products says

## Slide 208: Fuel Cell
High availability, high 9s, premium power, computer grade, or uninterruptible electricity, no matter what term you use, there is only one on site power plant with guaranteed availability beginning at six 9s, 99.9999% uptime

## Slide 209: Fuel Cell
Matching high availability electricity with high availability computers allows web hosting centers, collocation centers, ISPs, ASPs, corporate data centers, and industrial process facilities to substantially increase uptime, thereby raising revenues and decreasing losses

## Slide 210: Fuel Cell
The clean and green Sure Power System is the primary power source for the critical load
The utility grid becomes a backup power source
The System is 100 to 1,000 times less likely to fail than static UPS, batteries, and standby diesel generators used today

## Slide 211: Fuel Cell

## Slide 212: Fuel Cell
An interesting idea
Check http://www.hi-availability.com/ for more information on this approach

## Slide 213: Dual Power Supplies
In some cases it is wise to run two independent power systems that duplicates all or part of what was just discussed
For example

## Slide 214: Dual Power Supplies

## Slide 215: Routing Power and Data Cables
Power and data cables must be separated from each other to prevent EMI in the data cable
There is no standard for this
Common practice says to do it this way

## Slide 216: Routing Power and Data Cables
Power Level | In Spaces | In Pathways
Less than 3 kva | 2 inches | 2 inches
3 to 6 kva | 10 feet | 5 feet
More than 6 kva | 20 feet | 10 feet

## Slide 217: PoE
PoE – Power over Ethernet was created to provide power to devices over the existing UTP cable
This includes many types of devices such as wireless access points and IP telephones
The standard for this is 802.3af
This standard was approved on 12 June 2003

## Slide 218: PoE
There are two elements to a PoE system
  PSE – Power Source Equipment
  PD – Powered Device
PSEs are devices such as switches with ports designed to deliver power
The PD could be any device that uses a RJ-45 connector to talk to the network

## Slide 219: PoE
That is any device that requires 15.4 watts or less of power
The voltage at the PSE is 48 volts
The standard has five power classifications
  0 – 15.4 watts
  1 – 4 watts
  2 – 7 watts
  3 – 15.4 watts
  4 – Not used yet

## Slide 220: PoE
Either of two sets of wires can be used to deliver the power
The first method, Alternative A, uses the data pins of 1, 2, 3, and 6
This is sometimes called phantom power

## Slide 221: PoE
The second method, Alternative B, uses the normally unused pins – 4, 5, 7, and 8
The power can be delivered by the switch or a device inserted into the line to provide power
Endpoint switches can use either alternative
Midspan inserted devices can only use Alternative B

## Slide 222: PoE

## Slide 223: PoE

## Slide 224: PoE

## Slide 225: PoE
In the case where the end point uses a 1000Base connection that requires all eight wires for the data the electrical power is delivered or floated along with the data
1000base devices can only be powered from the end point, never by a midspan device

## Slide 226: PoE
The standard includes protection to prevent other devices such as printers from being damaged by connection to a PSE port
The PSE only sends electrical power down the cable if the device at the other end asks for it

## Slide 227: PoE
The 802.3af standard uses a DC detection technique to determine whether a powered device is attached and to which power classification the device belongs
A DC voltage is applied between the transmit and receive pairs
Then either the received current or voltage is measured

## Slide 228: PoE
To deliver power to a port a PSE will expect to see a 25K Ohm resistance between the pairs for the device to be considered a valid powered device
If the PSE does not detect a valid 25KOhm resistor, power is not applied to the port

## Slide 229: PoE
Once a powered device has been detected, the PSE may perform powered device classification
This is done by the PSE applying a DC voltage and current to the port

## Slide 230: PoE
If the PD supports optional power classification it will apply a load to the line to indicate to the PSE the classification the device requires by attenuating the DC voltage
The PSE then determines the powered device’s power classification using the Volt-Amp slope returned by the powered device’s signature

## Slide 231: PoE
If the powered device does not support classification, the powered device is assigned to Class 0
Each PSE must maintain a power budget
This is the maximum amount of power the PSE is rated to deliver
If the number of devices asking for power exceeds this budget, then one or more devices will not be provided with power

## Slide 232: PoE
Keep this in mind when troubleshooting device failures
The standard also includes methods for determining that a power capable PD has been disconnected and a non-power capable device has been plugged in
Basically when the link status goes down, power is disconnected

## Slide 233: PoE
A potential problem with powering all network connected devices is the wiring closet power requirements that result
With a large number of PDs the electrical service to the wiring closet may grow from a 15 amp circuit to a 50 amp circuit
Office buildings do not have that type of power to the wiring closets

## Slide 234: PoE
For example, if 240 devices require power, such as VoIP telephones, 3,695 watts of power would have to be delivered to the end point devices
In addition the typical switch requires 1,000 to 2,000W
This yields 5,000 to 6,000W of power
A 110 volt 15 amp circuit can provide 1,650W

## Slide 235: PoE
To upgrade this circuit the cabling will have to be replaced
Even that has a limit when dealing with 110 volt circuits
The maximum 30 amp circuit can deliver 3,300W per circuit
In addition to the electrical power requirements, the heat load will increase

## Slide 236: PoE
IDFs, for example, may become too warm without supplemental air conditioning

## Slide 237: PoE+
Even worse for heat loading is the revision to PoE that the IEEE is working on
POE+ or 802.3at is expected to deliver up to 30W per port
At this power level there are questions as to the ability of standard copper cables to handle this heat load
In addition, this will require even more power to the LAN room

## Slide 238: PoE+
The IEEE, TIA, and ISO are looking into this heat problem
A TSB from TIA is expected
Right now the thinking is a maximum heat rise of 10 degrees C will be allowed, up to an absolute of 50 degrees C

## Slide 239: New Versions of PoE
Some new versions of PoE are being discussed according to a webinar by Microsemi

## Slide 240: New Versions of PoE

## Slide 241: New Versions of PoE

## Slide 242: New Versions of PoE

## Slide 243: New Versions of PoE

## Slide 244: New Versions of PoE

## Slide 245: New Versions of PoE

## Slide 246: New Versions of PoE

## Slide 247: New Versions of PoE

## Slide 248: Floor Covering
Generally speaking for the average LAN room I do not think it makes much difference what is on the floor from concrete to carpet
And since I never wear shoes while working and sometimes take off my socks as well I am partial to carpet everywhere

## Slide 249: Floor Covering
But technically speaking this is a poor choice, even the very short pile office type carpeting, as any carpet will build up static electricity
I have yet to zap anything in the office environment, although I have ruined a couple of things at home
So let’s go over what you should do

## Slide 250: Floor Covering
Don’t do what I do as carpet, socks, and cool dry air are not a good combination
ESD is the concern
This is electrostatic discharge
ESD occurs when one material has an excess of electrons and another device has too few

## Slide 251: Floor Covering
When the two get near each other, nature seeks to achieve a balance
This balancing act is the spark from the ESD

## Slide 252: Floor Covering
Methods to use to reduce this risk include
  Tile
  Linoleum
  Metallic Tiles
  Antistatic Mats
  Table Mats

## Slide 253: Floor Covering
Tile means just normal floor tile
It is less likely to build up static than carpet
The same is true of linoleum
More fancy are metallic tiles which are grounded to the power supply for the room
If you do not want to change the existing floor covering, antistatic mats can be grounded through a screw on a wall socket

## Slide 254: Floor Covering
Table mats do the same thing
The only difference being you stand on the antistatic mat, whereas the equipment stands on the table mat
If you don’t want to do any of these, you can always use a wrist strap or ankle strap

## Slide 255: Physical Security
How physically secure the site should be depends on the level of risk and the tolerance to loss that can be tolerated
Security must take into account access to the site in all four dimensions
  The door
  The floor
  The walls
  The ceiling

## Slide 256: Physical Security
In some cases as was seen before there is no security
All equipment is just placed on a table or desk out in the open
This is poor practice because anyone, disgruntled employee or upset customer, can easily get to this equipment

## Slide 257: What’s Wrong Here
The following picture is from the Cisco Networking Academy website
This is the program that trains future network administrators
What’s wrong with this picture

## Slide 258: What’s Wrong Here

## Slide 259: The Door
The first thing to do is to secure the door
A latch should be put on the door to control access so as to restrict access to certain individuals and certain times of the day, such as a card reader as shown next
The reader is the small gray device to the left of the door
These systems cost from $1,000 to $2,000 in year 2000 prices in most cases

## Slide 260: The Door

## Slide 261: The Door
A combination lock system could also be used
If so, issue a different combination to each user, and issue new combinations periodically and whenever a combination is compromised
Have a procedure in place that revokes user access when a user leaves the company

## Slide 262: The Door
Use a lock that has a shield so that only the user entering the combination can see the keypad
Configure the lock to record an event log of users entering the locked area
You can also use a door camera to further document the user and any guests who enter with the user

## Slide 263: The Door
Use a metal or solid core wood door that's substantial enough to resist being forced open by shoulder impact
Reinforce the doorframe and strike plate to further resist shock loads and prying
Locate hinges so that intruders can't remove hinge pins from outside the door, or use nonremovable hinge pins

## Slide 264: The Door
Use long screws to attach hinges and strike plates to the surrounding wall structure
Also use one-way screws that cannot be removed
Weld the nuts onto any bolts that extend through the surface of steel doors
For fire doors and secondary exits equip the door with an alarm unit and heavy-duty lock

## Slide 265: Floor/Wall/Ceiling
What the floor, walls, and ceiling are made of is also very important
For example, a few years ago I was moving into a new building
For reasons I still do not understand we were moving in before the building was finished
When I went to open the door to my office, I found it locked and no key

## Slide 266: Floor/Wall/Ceiling
As I was complaining about this an electrician walked by
He said no problem I'll open it for you
So he set his ladder down, picked up a short piece of electrical conduit, climbed the ladder, and opened the door by raising the ceiling tile up and reaching over the wall to push down on the door handle
It took him about one minute to do this

## Slide 267: Floor/Wall/Ceiling
As you can see a false ceiling is no security at all
Besides opening doors, someone can just crawl over the top of the wall and drop into the room

## Slide 268: Floor/Wall/Ceiling
Typical office walls are no barrier either
Have you ever had to repair a hole in the wall caused by children playing
Even better, have you ever made a hole in the wall to hang a picture
Wallboard can be penetrated in just a few minutes

## Slide 269: Ventilation System
Secure any vents that lead into the data center
This could be inside the building or a roof vent
Inspect these areas periodically to be sure no one is slowly working on them

## Slide 270: Signs
Signs and wall maps that say here is where all of the really expensive equipment is located are a poor idea as well

## Slide 271: Location in the Building
If possible keep the data center away from areas where it will share a wall with an unused space or exterior wall
People have been known to just back a vehicle through an outside wall
Windows are always a bad idea
Try also to avoid high traffic areas
You want a stranger to be noticed

## Slide 272: Cabling Security
Security for the cabling system may be a consideration as well
Cables can be tapped physically or by sensing the EMI they put off
Conduit may be run throughout the building to help prevent this
However, this is quite expensive

## Slide 273: Electrical Power Security
If local codes allow, secure the electrical panels that feed the area
Some will turn the power off hoping the security system will be disabled as well
Of course if the security system has a battery backup, test it

## Slide 274: Surveillance
Keep an eye on things with cameras feeding to a video recorder
Use obvious ones and hidden ones
Consider combining door switches, motion detectors, sound-discrimination sensors, photocell beams, proximity switches, IR sensors, and cabinet-door switches into a comprehensive detection system

## Slide 275: Surveillance
Carefully control information about the details and location of any surveillance devices that you install

## Slide 276: Remote Access
Logging into equipment from home in the middle of the night is a lot more convenient than driving into work
However, what is convenient for you is also convenient for everyone else

## Slide 277: External Monitoring
You should be using a program to monitor server responsiveness and report offline servers, stopped services, and so on
However, this is probably a device in the data center
So, set up a secondary monitoring node outside the server room

## Slide 278: External Monitoring
This unit will sound the alarm if an intruder disables the network connection or shuts down the primary unit to prevent notification pages from getting out of the server room

## Slide 279: Inventory and ID Tags
Keep an inventory of all computer equipment that someone could remove
Such as servers, disk drives, and monitors
Attach asset tags or other markings to these devices
Compare actual equipment with asset records annually

## Slide 280: Security
I am not talking about keeping professional spies out, just the use of common sense based on the amount of loss that can be tolerated

## Slide 281: Earthquake Zones
In earthquake prone areas equipment must be installed according to the Uniform Building Code requirements for seismic anchorage or the more stringent NEBS – Network Equipment Building System requirement in GR-63-CORE

## Slide 282: Markets Other Than the US
If you do work in other markets be familiar with
  Canada – CSA standards
  European Union – CENELEC and EN standards
  Australia/New Zealand – AS/NZ standards
  Everywhere Else – ISO/IEC standards
  Many countries publish additional national standards

## Slide 283: For More Information
Build the Best Data Center Facility for Your Business
  Douglas Alger
  ISBN 1578051826
Network Cabling
  Chris Clark
  ISBN 0072132337

## Slide 284: For More Information
Cabling: The Complete Guide to Network Wiring
  David Groth and Jim McBee
  ISBN 0782126456
The Cabling Handbook - 2nd Edition
  John R. Vacca
  ISBN 0130883174

## Slide 285: For More Information
The Telecommunications Industry Association
  http://www.tiaonline.org/index.cfm

## Slide 286: For More Information
Sean Donelan, a frequent contributor to the NANOG newsgroup suggests these sources for questions on electrical grounding in particular, electrical and other cabling installation in general

## Slide 287: For More Information
He wrote in a message from April 2002
  While working at a previous employer, I had the privilege of hiring Ralph Morrison to look at grounding in our facility
  I spent some time with Mr. Morrison talking about different methods used in large installations
  It was a great learning experience
  If you don't know Mr. Morrison, check out a few of his books on the subject

## Slide 288: For More Information
Specific sources he said to look at include
  BICSI, Telecommunications Cabling Installation Manual
  NFPA 70, National Electrical Code
  IEEE Std 1100, IEEE Recommended Practice for Powering and Grounding Sensitive Electronic Equipment
  IEEE Std 142, IEEE Recommended Practice for Grounding of Industrial and commercial Power systems

## Slide 289: For More Information
  Mil HDBK 419, Grounding, Bonding, and Shielding for Electronic Equipment and Facilities

## Slide 290: For More Information
And these
  Federal Information Processing Standards Publication 94, Guideline on Electrical Power for ADP Installations (A bit out of date, but explains where some of the weirder stories come from)
  TIA/EIA-568-A, Commercial Building Telecommunications Cabling Standard

## Slide 291: For More Information
  TIA/EIA-569-A, Commercial Building Standard for Telecommunications Pathways and Spaces
And a few more
  TIA/EIA-570-A, Residential and Light Commercial Telecommunication Wiring Standard
  TIA/EIA-607, Commercial Building Grounding/Bonding Requirements for Telecommunications

## Slide 292: For More Information
  TIA/EIA-758, Customer-Owned Outside Plant Telecommunications Cabling Standard
  IS0/IEC 11801, Generic Cabling for Customer Premises