## Slide 1: How to Terminate a Corning Unicam Connector Last Update 2008.08.18 1.1.0

## Slide 2: Objectives
Learn how to install a Corning Unicam connector onto fiber optic cable

## Slide 3: What is a Unicam Connector
Rather than the often difficult and frequently time consuming termination of a fiber optic cable using a hand polish method, the Corning Unicam system requires a comparatively simple mechanical splice
This attaches a fiber optic cable to a connector, just as a mechanical splice connects two fiber optic cables together

## Slide 4: What is a Unicam Connector
This makes field termination of fiber optic cables much easier and quicker
The connector is premade with the end polished and a fiber stub connected
The termination process only requires the fiber optic cable be connected to this fiber stub
The disadvantage is the higher loss and cost of materials

## Slide 5: What is a Unicam Connector
This type of connection is perfectly suitable for multimode cable used inside a building, such as for a backbone connection between telecommunication rooms
The added loss is insignificant in this case
As few connections are required the added cost is tolerable

## Slide 6: What is a Unicam Connector

## Slide 7: Typical SC Connector

## Slide 8: Steps in Termination
Place the connector in the tool
Prepare the fiber optic cable
Terminate the fiber optic cable
Attach the remaining parts

## Slide 9: Place the Connector in the Tool
The Corning video explains this process better than a written explanation can, so go watch it
The basic process is
  Slide the VFL coupler up to the top of its travel
  Release the load button
  Push the cradle to the bottom of the tool
  Press the reset button
  Turn on the power

## Slide 10: Place the Connector in the Tool

## Slide 11: Place the Connector in the Tool
Be sure the connector parts are aligned correctly
  The cam is open when the cam key is 90 degrees from the date code when it is facing up
Remove the dust caps at both ends of the connector

## Slide 12: Place the Connector in the Tool

## Slide 13: Place the Connector in the Tool
Squeeze the load button to move the cradle away from the wrench

## Slide 14: Place the Connector in the Tool

## Slide 15: Place the Connector in the Tool
With the date code up, place the connector in the tool by first placing the lead in tube into the wrench
Slowly release the load button while guiding the connector into the cradle

## Slide 16: Place the Connector in the Tool

## Slide 17: Place the Connector in the Tool
Continue sliding the coupler down until the connector is seated in the tool
To check that the connector is in the proper location, close the cover of the tool
If the error light stays off, then the connector is in the correct location

## Slide 18: Error Light
If the error light flashes, try again
  The usual problem is the connector is not all the way down toward the bottom of the tool
  or
  The VFL Coupler has not been pulled down to hold the end of the connector

## Slide 19: Prepare the Fiber Optic Cable
To prepare the fiber for termination
  Slide the boot onto the fiber
  Remove the fiber jacket
  Place two marks on the fiber buffer
  Remove the outer layers on the fiber
  Clean the fiber
  Cleave the fiber to create a proper end for joining to the connector

## Slide 20: Slide the Boot On
Slide the boot onto the fiber

## Slide 21: Slide the Boot On

## Slide 22: Jacket Buffer Coating
There may be up to three outer covers on a tight buffer fiber optic cable
These are the
  Jacket
  Buffer
  Coating
These vary in size
The jacket in particular will vary over a wide range of sizes

## Slide 23: Jacket Buffer Coating
The buffer and coating are more uniform
Here is what the look like in comparison

## Slide 24: Jacket Buffer Coating
Jacket
Coating
Buffer

## Slide 25: Remove the Jacket
The Jacket Stripping removes the jacket from the cable if there is any
The jacket is the colored plastic cover
Cable jackets come in various sizes
A common size is nominally 3 mm in diameter
Smaller ones are supposed to be 900 microns, which just short of 1 mm

## Slide 26: Remove the Jacket
However, in practice these do no measure quite that exactly
Regardless of the actual size, just use the opening in the Jacket Stripping tool that best matches the size of the jacket
The tools provided for this purpose are not made just for this
Typically the are made for electrical cable

## Slide 27: Remove the Jacket
On these tools the AWG 10 size hole is 2.6 mm, which is about right for the larger cables
The AWG 18 or 20 holes work for the 900 micron jackets
The others are in between at 12, 14, or 16 AWG

## Slide 28: Remove the Jacket
To remove the jacket
  At a point about 50 mm from the end of the fiber optic cable close the tool jaws over the jacket while holding the tool perpendicular to the cable
  Squeeze the jaws shut to cut through the jacket while rotating the tool slightly to cut all of the jacket
  Remove the tool
  Slide the jacket off by hand

## Slide 29: Jacket Tool

## Slide 30: Removing the Jacket

## Slide 31: Places Two Marks on the Cable
Two marks are placed on the fiber to ensure the fiber is properly placed in the cleaving tool
Place a mark on the fiber at 40 mm
Place another mark on the fiber at 51 mm or 11 mm further back than the 40 mm mark

## Slide 32: Place Two Marks on the Cable

## Slide 33: Remove Outer Layers
Once the jacket is out of the way the outer layers of the actual fiber must be removed
The Fiber Optic Stripping tool is used for this
The first outer layer is the plastic buffer
This is a colored plastic cover
The inner coating is not colored as it is part of the fiber optic cable itself

## Slide 34: Fiber Optic Stripping Tool

## Slide 35: Removing the Buffer

## Slide 36: Removing the Buffer

## Slide 37: Removing the Buffer
About 5 mm from the end place the fiber in the large V-notch of the tool
Align the tool perpendicular to the fiber
Squeeze the tool shut
Pull the tool to remove the buffer
Move in about 5 mm more
Pull the tool to remove the buffer
Continue until you reach the 40 mm mark

## Slide 38: Remove the Coating
Place the bare fiber optic cable in the small V-notch
Align the tool perpendicular to the fiber
Squeeze the tool shut
Pull the tool to remove the coating in a single pull
The problem here is not breaking the fiber
In which case you must begin again

## Slide 39: Clean the Fiber
Once the outer layers of the fiber are removed the fiber itself must be cleaned
Fold a fiber optic cable cleaning wipe in half
Dampen a the wipe with the fiber cleaning fluid by pressing the wipe down on the fluid container twice
Pull the wipe over the fiber to clean it

## Slide 40: Cleave the Fiber
To cleave the fiber
  Clean the channel in the cleaving tool where the fiber will be placed
  Squeeze buttons A and B to open the clamps on the tool
  Place the fiber in the slot
    The bare fiber should be in the V groove
    The edge of the coating is aligned with the alignment mark
    The fiber rests under the tab

## Slide 41: Cleave the Fiber

## Slide 42: Cleave the Fiber
Release the B button
Release the A button
Be sure the fiber is held by both clamps
Turn the knob 360 degrees to cleave the fiber
Squeeze the A button to remove the cut off fiber
Dispose of this scrap

## Slide 43: Cleave the Fiber

## Slide 44: Cleave the Fiber
Hold the fiber
Squeeze button B
Remove the fiber

## Slide 45: Terminate the Fiber
Insert the cleaved fiber into the back of the lead in tube on the termination tool setup earlier
Insert it until slight pressure is felt as the fiber end contacts the fiber stub on the connector placed in the tool
The mark on the cleaved fiber should be within 2 mm of the lead in tube

## Slide 46: Terminate the Fiber
While maintaining enough pressure to create a slight bend in the fiber, squeeze the cam button until it locks

## Slide 47: Terminate the Fiber

## Slide 48: Terminate the Fiber
If the green light is lit, the termination was successful
Turn the crimp knob 180 degrees in either direction
Open the cover
Slide the VFL coupler all the way to the top of the tool
Slightly squeeze the load button to remove the connector

## Slide 49: Terminate the Fiber
Press the reset button

## Slide 50: Terminate the Fiber

## Slide 51: Terminate the Fiber

## Slide 52: Attach the Remaining Parts
Install the end dust cap
Slide the boot up onto the back of the connector until it reaches the cam
Install the outer shroud by lining up the date code with the key side of the shroud
Using the boot push the connector onto the shroud until it snaps in place

## Slide 53: Attach the Remaining Parts

## Slide 54: Review
The best review is to use the tool, so get to work