## Slide 1: Structured Cabling Implementation Last Update 2014.10.01 1.19.0

## Slide 2: Objectives
Learn how to properly install LAN cabling

## Slide 3: Planning
Now being familiar with the basic parts of a LAN
As well as having read all of the standards discussed above, you are ready to plan a cabling job

## Slide 4: Planning
The main steps are
  Project planning
  Site survey
  Making a parts list
  Making a tools list
  Ordering and checking parts and tools

## Slide 5: Project Planning
The general tasks called for in a cabling project include
  Decide how to secure the cable for its horizontal runs
  Make sure the correct length and types of cables are available on site
  Secure the needed pulling tools, equipment, and supplies
  Identify the locations to be used to access and pull the cable

## Slide 6: Project Planning
  Obtain equipment to allow communication among those doing the installation

## Slide 7: Site Survey
A site survey includes
  Distances to be covered
  Nature of the building construction
  Existing cabling

## Slide 8: Distances to be Covered
Cabling is not terribly expensive these days, but you still do not want to buy more than is required
So the first step is to get or create a floor plan of the building to be cabled
On this floor plan mark where each device that will be connected to the network will be, as well as the LAN room

## Slide 9: Distances to be Covered
Devices include things like
  PCs
  Printers
Then measure or estimate the distance of each cable run
Also walk through the building to be certain these planned routes will work
Things get in the way

## Slide 10: Building Construction
By this I mean if you are lucky the building is of modern construction were the ceiling is made of suspended ceiling tiles
There is nothing in the space above the tiles, such as insulation
The walls are made of wallboard attached to metal studs, with no cross bracing
If so, installation will proceed as discussed below

## Slide 11: Building Construction
If not, well that’s why they invented outsourcing
Potential problems include
  Solid concrete walls
  Granite walls, as in the lobby of an office building
  No false ceiling

## Slide 12: Building Construction
There are ways around all of these problems, but none look very good and all raise the cost
The point is check for these potential problems first
Lets Look at some examples of common problems

## Slide 13: Solid Concrete Wall

## Slide 14: Ceiling Full of Insulation

## Slide 15: Sheetrock on Metal Studs
The easiest type of construction to cable in is sheetrock covered walls built with metal studs
These do not require any cross bracing between the studs
This makes dropping or placing the cable much easier
For example

## Slide 16: Sheetrock on Metal Studs

## Slide 17: Top Plate

## Slide 18: Hole

## Slide 19: Existing Cable
The NEC now calls for unused cabling to be removed whenever new cable is put in
This requirement can significantly increase the cost of any cable installation
The NEC in Articles 770.2, 800.2, and 830.2 defines what cable that must be removed constitutes

## Slide 20: Existing Cable
Each of these sections discusses a different kind of cable, with 800 being the most relevant
Basically NEC 800.2 says that any cable that is unterminated and not marked as being for future use must be removed
But removed only from those spaces that are accessible without damage to the building structure or finish

## Slide 21: Existing Cable
The thrust seems to be removing this cabling only when renovation is going on
But watch the interpretation of this as it develops
The cost of this can be quite high

## Slide 22: Making a Parts List
From the site survey list all of the parts needed
The parts are discussed in detail later in this presentation

## Slide 23: Making a Tools List
Based on the nature of the building and the staff available make a list of the tools required to install, terminate, and test the cable
For example
  Ladders
  Cable pulling poles
  Safety equipment
  And so forth

## Slide 24: Ordering Stuff
Local suppliers can be found in the Yellow Pages
Even places like Lowes and Home Depot are beginning to stock some of these parts
Mail order suppliers vary, search the web or check the ads in the major trade publications

## Slide 25: Checking Stuff
When everything arrives, check it
  Is it what was ordered
  Was everything included
  Is anything broken

## Slide 26: Steps in Cable Installation
The next step is to actually install the cabling system
A typical job involves these basic steps
  Install the cables in the ceilings and walls
  Install the stuff needed to terminate the cable in the LAN room
  Terminate the cable in the LAN room
  Terminate the cable in each workspace
  Test it

## Slide 27: Installing the Cables
Selecting and installing cables involves
  Selecting the correct cable
    Category of cable
    Plenum or non plenum cable
  Installing the cable
    Methods
    Precautions

## Slide 28: Use the Correct Cable
Solid wires are used to connect work areas to the LAN room as stranded wires attenuate faster
By solid I mean that each of the eight wires is a single piece
Stranded wire is used for patch cables, as it is easier to manage for this use only, where the cables are never very long

## Slide 29: Use the Correct Cable
By stranded I mean that each of the eight wires is made up of several individual wires, but there are still only eight wires

## Slide 30: Use the Correct Connector
In addition to the correct type of cable, use the correct style of connector
AMP says
  The conventional plug has in-line insulation displacement contacts that pierce the middle of the insulation and stranded wire when crimped
  RJ45 plugs designed for solid conductors have offsetting contacts that straddle and wedge the cable’s solid conductor

## Slide 31: Use the Correct Connector
  If a RJ45 plug designed for stranded conductors is crimped onto solid conductors, the blade’s piercing teeth will be deflected and bent by the cable’s center conductors resulting in an intermittent connection
  However, the newer tri-point plugs are designed for both stranded and solid conductors and will successfully terminate both types of conductors

## Slide 32: Color of Cable
It makes no difference what color the cable is that runs through the walls and ceiling

## Slide 33: Plenum Cables
Besides the categories cables are also rated based on their flammability, heat resistance, and how much visible smoke – in the case of plenum rated cable – they generate when exposed to a flame
Plenum cable may be used in the plenum space and as riser cable
Plenum rating includes any nonmetallic cable ties and other support devices

## Slide 34: Plenum Cables
The plenum is the space between the structural ceiling in a building and any false ceiling that may exist, or any other space that holds breathable air
This space is used for air ducts and to carry return air to the HVAC system

## Slide 35: Plenum Space

## Slide 36: Plenum Space
Structural Ceiling
Top of Light Fixture
False Ceiling

## Slide 37: Distance Limitations of Cable
For horizontal cable runs from a telecommunications closet to a work-area outlet, the maximum transmission distance allowed for UTP cable is 90 meters or 295 feet
This is from the port in the wall in the work area to the port in the patch panel in the LAN room
This link is called the permanent link

## Slide 38: Distance Limitations of Cable
An additional 10 meters or 33 feet provides for patch cords both in the work area and the LAN room
This yields the maximum distance for UTP cable of 100 meters or 328 feet from NIC to switch
This is called the channel

## Slide 39: Distance Limitations of Cable
This distance limitation is due to the attenuation of the signal in the cable due to the twisting of the cable
This total distance of 100 meters was originally created for network control
Half duplex Ethernet relied on collision detection mechanisms to prevent some errors on the shared network

## Slide 40: Distance Limitations of Cable
By limiting the cable to this distance all stations on the shared network were able to hear and recover from collisions
With the advent of full duplex Ethernet this should have gone away
However, NICs were designed to only generate a signal powerful enough to reach 100 meters

## Slide 41: Distance Limitations of Cable
In addition, twisted-pair cable is not manufactured to as strict standards as is say coaxial cable.
Sending high-frequency electrical signals over twisted-pair cabling is difficult as the lack of shielding means the signals have to deal with a harsher electrical environment

## Slide 42: Distance Limitations of Cable
Increasing the distance would have required changes to the basic design of NIC circuits and a different type of cable as they were designed to send data up to 328 feet or 100 meters
In addition, the higher power levels were seen to introduce interference on the lines from noise produced at these higher power levels

## Slide 43: Distance Limitations of Cable
There is a minimum distance for cables, including patch cables, especially for higher speed networks
  Cable runs must be longer than 20 meters
  Patch cables should be longer than 8 feet
These minimum distances are commonly ignored
Two reasons are advanced for these minimum distances

## Slide 44: Distance Limitations of Cable
One is due to the restrictions of cable testing equipment
This equipment cannot test cable any shorter than this
The other is the short link phenomenon
Which says that a cable shorter than this can show too much crosstalk

## Slide 45: Distance Limitations of Cable
This is because most crosstalk is generated near the connectors where the cable is untwisted
This high level of crosstalk throughout the length of a short cable as opposed to just near the connector, may be interpreted by the electronics as collisions when run at higher loads or speeds

## Slide 46: Cable Installation Precautions
It is vital to use proper installation practices to ensure the performance of the entire system is not diminished simply through improper installation
Using a Category 5 system as an example, any one of the following practices may not, by itself, reduce a system below Category 5 compliance

## Slide 47: Cable Installation Precautions
Since many of these items such as pulling cables and untwisting pairs are unavoidable, care must be taken not to allow their combined effect to lower the performance of the system

## Slide 48: Pulling on Cable
One of the first installation tasks is pulling cables from the telecommunications closet to each outlet location
The maximum pulling tension for Category 5 is 25 lbf
Higher tension on the cable may stretch the twists, or in effect, untwist the pairs
Extreme tension will also increase attenuation

## Slide 49: Pulling on Cable
Visual inspection of an installed link cannot identify that tension limitations have been exceeded
Using proper pull techniques, pull cords, and cable lubricants will prevent this type of damage
The most common method of pulling a cable is a pole of some sort, such as the following

## Slide 50: Cable Pulling Pole

## Slide 51: Cable Bend Radius
Extending a cable from a closet to an outlet may involve going through walls, ceilings, floors, conduits, ducts, raceway, corners, or other bends
It is crucial not to exceed the minimum bend radius of the cable being installed
Four-pair Category 5 cables must keep the bend radius for each turn in excess of one inch

## Slide 52: Cable Bend Radius
Multipair Category 5 cables – those with more than 4-pairs - have a minimum bend radius of 10 times the outside diameter of the cable
Tight bends will force the pairs in a jacket to lay flat, or untwist, which may increase crosstalk at that point

## Slide 53: Follow These Guidelines

## Slide 54: Interference
What the cable encounters in its journey from wiring closet to end user area is also important
Not being shielded UTP cable is susceptible to outside interference such as EMI

## Slide 55: Interference
Common sources of EMI in a typical office environment include
  Motors
  Heating and air conditioning equipment
  Fluorescent lights
  Photocopiers
  Elevators
  Electrical wiring
  TVs
  Some medical equipment

## Slide 56: Interference
Avoid running the data cables too near these types of devices
The guidelines for the amount of separation are in the NEC and BICSI’s Telecommunications Distribution Methods Manual
Further, the type of device has an impact on the separation required

## Slide 57: Interference
Do not place UTP cable in the same raceway or through the same hole in the top plate of a wall as the AC power line is run
When running near or crossing a power wire the separation to maintain depends on the type of circuit
For example a common 120 volt circuit requires 2 inches of separation

## Slide 58: Interference
Whereas, 208 volt single phase circuit requires 2 feet of separation
High temperature also causes attenuation to go up

## Slide 59: Interference
Here are some tables with guidelines on distances from an article from a BICSI publication from October 2014 by Tim West
The b note in the second table means you need to test for each situation

## Slide 60: Interference

## Slide 61: Interference

## Slide 62: Interference

## Slide 63: Alien Crosstalk Mitigation
With the increase in speed over copper cables seen in 1G and 10G networks some are suggesting that the nice, neat installation practices used to date be abandoned
The idea being that this helps to introduce alien crosstalk

## Slide 64: Alien Crosstalk Mitigation
By laying the cables at random in a cable tray, avoiding nice tight cable ties, and by spreading out the cables this type of interference is mitigated
Maybe, maybe not

## Slide 65: Proper Support
UTP cable should be placed at the top of the plenum space held in place and supported by using J hooks, a ladder rack, or any other system that eliminates excessive sag and keeps the cable away from sources of interference
Support should be provided every 4 to 5 feet

## Slide 66: Proper Support

## Slide 67: Common Supporting Devices

## Slide 68: Firestop
A firestop refers to the installation of qualified firestop material in any holes made through fire-rated floors, walls, or ceilings for the penetration cables
Firestopping is used to buy time in the event of a fire
Most common requirements are for 1, 2 or 3 hour rated materials
Firestops can be divided into two types

## Slide 69: Firestop Material
Mechanical systems are components pre-sized and shaped to fit around standard cables, tubes, and conduits
These products are made of flexible substances that look like rubber
This type of system uses mechanical pressure to hold the firestop components in place and provide a tight seal around the cables

## Slide 70: Firestop Material
Nonmechanical firestop systems are generally pliable, such as putties, caulks, blankets, silicone foam and other types of materials that can be molded to fit into an opening to seal it

## Slide 71: Mechanical

## Slide 72: Mechanical

## Slide 73: Mechanical

## Slide 74: Putty

## Slide 75: This Will Not Work

## Slide 76: This Will Not Work

## Slide 77: Firestop Material
As an article in the BICSI News says
  Most of today’s firestopping systems employ intumescent materials that, when exposed to heat, expand to fill a void in the penetration
  Mechanical systems such as sleeves will contain, control and direct the expansion of this intumescent material
  A series of small holes offer many benefits over one large hole

## Slide 78: Firestop Material
  Commonly used materials include
    Firestop mortar and caulk are semi-permanent products
      Caulk is applied to the penetration with a caulk gun
      Putty sticks are manually molded around cables, conduit, and pipes
      Putty is the most desirable of the semi-permanent intumescents
      Take care not to contaminate the putty when re-entering a system
      Do not lay it down in the ceiling
      Use a plastic bag and seal it up until you are ready to re-install it

## Slide 79: Firestop Material
      Firestop blocks and pillows contain intumescent material and are typically stacked and otherwise fitted into large penetrations
      This method may require the use of chicken wire anchored to the wall to contain and control the expansion of the intumescent
      Compression guidelines should be followed if pillows are removed
  Although the products listed above are effective as firestop materials, moving, adding or changing cables can compromise their effectiveness

## Slide 80: Cable Trays and Firestops
There are two ways to carry wires in cable trays through a firewall
  Stop the tray at the firewall, then use a mechanical sleeve to carry the cables through the wall
  Extend the cable tray through the firewall, then fill the void in the wall with firestop material

## Slide 81: Cable Trays and Firestops
As the BICSI newsletter said where high volumes of cables are installed, cable trays are a common method of conveying cables through a facility
Cable trays require relatively large opening and specific firestop solutions
Firestopping pillows are an excellent choice for sealing cable tray penetrations

## Slide 82: Cable Trays and Firestops
They are easy to install and do not require a high degree of skill
Pillows can be easily removed and reinstalled, making cable changes fairly easy
Thin firestopping panels called intumescent composite sheets are also a good choice for sealing off large areas around cable trays

## Slide 83: Firestop Options
Here is summary table of the possible types of firestops from an article from the BICSI news periodical from May/June 2014

## Slide 84: Firestop Options

## Slide 85: Firestop Options

## Slide 86: Firestop Options

## Slide 87: Firestop Categorization
Firestopping systems are typically categorized by one or more of the following ratings, according to UL 1479
  Flame
    The F rating (FH in Canada) is expressed in hours
    This number indicates the specific length of time that a barrier can withstand fire before being consumed or before permitting the passage of flame through the opening
    This rating was designed to save property

## Slide 88: Firestop Categorization
  Temperature
    The T rating (FTH in Canada) is expressed in hours and indicate the length of time that the temperature on the nonfire side of the penetration does not exceed 325 °F above the ambient temperature
    This ensures that the temperature on the side of the wall away from the flame does not reach the flash point of any materials on that side of the wall
    This rating also is designed to save property

## Slide 89: Firestop Categorization
  Smoke
    The L rating (U.S. and Canada) is the amount of air (and thus cold smoke) that can leak through a penetration, measured in cubic feet per minute
    The test is administered at ambient temperature and at 400 °F due to the actual performance of firestop materials at different temperatures
    While L ratings are currently rarely seen in the field, insurance risk assessments have found leakage to be the single biggest contributor to loss of life in a fire
    This rating was designed to save lives

## Slide 90: Firestop Categorization
Through-wall penetration firestop devices may also be tested to UL 2043 as to their suitability for use in air handling spaces
This test measures the rate of heat release and the optical smoke density of a burning sample

## Slide 91: Firestop Operation
When the temperature from a fire reaches approximately 375°F, the intumescent material begins to expand
Unrestrained, this material will expand from six to 12 times its initial volume
In an enclosed space, it creates a hard char similar to lava rock that fills the void created when cable jackets burn away, blocking the path of the fire

## Slide 92: Plastic Sleeves
If a plastic sleeve is used for the cables, which is a really bad idea, a firestop that will apply pressure to the wall from the outside must be used in order to compensate for the melted plastic sleeve

## Slide 93: Firestop Standards
Two standards relate to firestopping
  NFPA 75
  FM Global Property Loss Prevention Data Sheet 5-32 – FM DS5-32

## Slide 94: Splicing
Do not splice a copper cable
If a cable is damaged, do not repair it
Replace the cable
In other words, every cable should be a single, unaltered piece from one end to the other
This is especially true of horizontal cables

## Slide 95: Cable Termination
Once the cable is installed it must be terminated
This is the process of installing connectors on each end of the cable
Yes, it works to just install RJ-45 male connectors on each end of the cable and plug one end into the NIC and the other end into the switch
If you do this, do not tell anyone I taught you anything

## Slide 96: Cable Termination
Leaving aside the fact that the RJ-45 male connector is designed for stranded, not solid cable, this practice
  Does not conform to the standards
  It looks terrible to anyone who knows what they are doing
  Makes it difficult to label the cable
  Makes troubleshooting harder
  So forth, and so on

## Slide 97: Cable Termination
There are two parts to cable termination, or rather two places where it must be done
  The LAN room
  In each work space
We will discuss the LAN room first

## Slide 98: LAN Room Cable Termination
As shown earlier, cable is typically installed by running it through the space between the false ceiling and the structural ceiling
This leaves all of the cables coming down out of the ceiling in a big bunch
There are two ways to bring these cables down into the LAN room

## Slide 99: Into the LAN Room
There is the wrong way

## Slide 100: The Wrong Way

## Slide 101: Into the LAN Room
There is the right way

## Slide 102: The Right Way

## Slide 103: The Right Way

## Slide 104: Into the LAN Room
Cabling does not have to come through the ceiling
In some cases it works best to come up through the floor
This looks better than a bunch of poles going from the ceiling to the desks
However it requires that you control the space on both floors

## Slide 105: Into the LAN Room
If the space is part of the slab, then this is considered to be a wet location – due to the nature of concrete and trapped water – the cable must conform to those conditions; which normal cable does not
Once the cable is in the room, something must be installed in the room to hold the stuff that will be used to terminate the cable

## Slide 106: In the LAN Room
In most cases this consists of what is seen next

## Slide 107: In the LAN Room

## Slide 108: In the LAN Room
The photograph just shown shows all of the elements required in a LAN room
Each of these will be covered in detail next
The elements are
  Relay Rack
  Patch Panel
  Cable Management

## Slide 109: Relay Rack
The easiest way to keep things straight is to place the equipment and devices in a rack
The most common type is called a Relay Rack
This unit is about seven feet tall and two feet wide
It is attached to the concrete floor with bolts

## Slide 110: Relay Rack
It is braced to the wall using a piece commonly called a ladder rack
Equipment is attached to the rack with machine screws

## Slide 111: Relay Rack

## Slide 112: Relay Rack Bolted to Floor

## Slide 113: Concrete Anchor

## Slide 114: Concrete Anchor With Bolt

## Slide 115: Concrete Anchor Installation

## Slide 116: Concrete Anchor Installation
For this lag shield type, drill a hole for the anchor, tap the anchor into the hole, position the relay rack, and install the lag screw to fasten the relay rack to the floor
Hold the rack tight against the floor and tighten the fastener until it is fully seated against the rack and secure in the hole
Don't over tighten it, or you may either break the fastener or ruin the anchor bond

## Slide 117: Ladder Rack Bracing

## Slide 118: Bonding and Grounding
To ensure the safety of the equipment and the personnel working with the equipment and to draw off noise from the transmission systems bonding and grounding must be done
These are two separate things done for different purposes

## Slide 119: Bonding and Grounding
The procedure as explained by Panduit is to
  Bond the equipment to the rack
  Ensure the racks have electrical continuity
  Bond the racks to the building grounding system
For example

## Slide 120: Equipment

## Slide 121: Racks

## Slide 122: Racks

## Slide 123: Building Ground System

## Slide 124: Bonding
Here are some slides on this from a webinar in August 2012 by Cabling and Installation and Maintenance magazine

## Slide 125: Bonding

## Slide 126: Grounding

## Slide 127: Bonding and Grounding

## Slide 128: Bonding and Grounding
In short the lack of bonding is a safety concern as you may become the path to earth producing a shock when touching the unbounded components
Whereas grounding is to remove noise and also for safety as it drains away transient currents

## Slide 129: Bonding and Grounding

## Slide 130: Bonding and Grounding

## Slide 131: Bonding
Let’s see how this is done
All conduits, cable trays, ladder racks, equipment racks and all other non-current carrying hardware should be bonded together at the TGB - Telecommunications Grounding Bulbar or TMGB - Telecommunications Main Grounding Bulbar

## Slide 132: Bonding
The TMGB must be grounded to the equipment ground bulbar in the main electrical panel or to an approved building grounding electrode system
Refer to ANSI-J-STD-607-A for details on how to perform these activities

## Slide 133: Bonding and Grounding
All parts of the system must be bonded together
This bonding does not mean to just bolt the parts to each other
Each connection between components must have a suitable ground connection such as a jumper as shown below from it to the bulbar

## Slide 134: Bonding and Grounding

## Slide 135: Data Center Bonding

## Slide 136: Data Center Bonding

## Slide 137: Bus bars in Data Center

## Slide 138: Relay Rack Bonding

## Slide 139: Relay Rack Bonding

## Slide 140: Ladder Racks and Cable Trays
These requirements apply to any ladder racks and cable trays used to carry cables around the data center
As the NEC says

## Slide 141: Ladder Racks and Cable Trays

## Slide 142: Bonding

## Slide 143: Bonding

## Slide 144: Equipment
Each piece of equipment needs to be attached to the same grounding system as directed in the user manual for it
For example
  The Gateway Series appliance must be properly earth grounded for safety reasons
  If the unit is not properly earth grounded, the unit and/or other equipment connected to the unit could be damaged

## Slide 145: Equipment
  If a Gateway Series appliance is damaged while it is improperly grounded, the warranty on the Gateway Series appliance is void
  A ground lug is located on the opposite side from the front panel of a Gateway Series appliance
  Attach an appropriate length and gauge of wire to the double-crimp ground ring terminal

## Slide 146: Equipment
  The wire length should be as short as possible, and gauge should be 18 AWG or greater
  Stranded or solid wire is acceptable
  Wire is not provided with the Gateway Series appliance
  Double crimp the ground ring terminal to the wire

## Slide 147: Equipment
  Next, slide the ground ring terminal over the ground lug
  Then fasten the ground ring terminal to the ground lug using the ground nut
  The ground nut must be turned clockwise to tighten it onto the ground lug
  The opposite end of the wire that is connected to the ground ring terminal should be securely fastened to an unpainted metallic section of a properly earth grounded equipment rack

## Slide 148: Equipment
  A connector for the opposite end of the wire is not provided with the Gateway Series appliance
  Note: Taking into consideration the requirements of all equipment that is connected to or sharing the rack, the equipment rack should be properly earth grounded
  Refer to the manufacturer of the rack for instructions on how to properly earth ground the rack

## Slide 149: Connect to the Building System

## Slide 150: Draining Currents to Earth
Once these transient currents are captured they must be effectively drained to the earth
This requires that the building grounding system to which the telecommunications grounding system is attached be connected to a properly designed ground field

## Slide 151: Ground Resistance
This is determined by the ground resistance

## Slide 152: Ground Resistance

## Slide 153: Ground Resistance
Ground resistance can be measured by an electrician using a test such as this

## Slide 154: Ground Resistance

## Slide 155: Ground Resistance
The ground resistance is determined by several factors some of which can be adjusted when the initial test shows the round resistance is not suitable, such as
  Size and depth of ground rods
  Type of soil
  Amount of moisture in the soil
  Temperature
  Salts in the soil

## Slide 156: Ground Rod

## Slide 157: Soil Type

## Slide 158: Moisture Level

## Slide 159: Temperature

## Slide 160: Salts

## Slide 161: Mounting Stuff
Things are mounted to a relay rack using Pan Head Machine Screws
  Of course any head style will work
The size is either a 10-32 or a 12-24 depending on the rack
  This refers to the diameter and thread pitch
They are ½” to ¾” long

## Slide 162: Mounting Stuff

## Slide 163: Relay Rack
The width inside the rack where the equipment is mounted is usually 19 inches
Some racks are 23 inches wide, especially those used with high price WAN equipment
Check the size of the equipment before having the rack installed

## Slide 164: Relay Rack
It is a good idea to document the layout of the boards in the switches and other configuration information
A copy of the manuals, especially the quick setup manual, should be stored here also
These can be stored on the Relay Rack itself

## Slide 165: Relay Rack

## Slide 166: Relay Rack - Wall Mount
Relay racks need not be seven feet tall and bolted to the floor
They can be any size
If they are shorter than seven feet, then they are usually bolted to a wall and swing out for access

## Slide 167: Relay Rack - Wall Mount

## Slide 168: Patch Panel
The cables themselves are terminated in the LAN room to the back of a board that has female RJ-45 jacks built into it or as modules that are plugged into it, after the cable is terminated into the modules
This board is called a patch panel
For example

## Slide 169: Patch Panel Front

## Slide 170: Patch Panel Front

## Slide 171: Patch Panel Rear

## Slide 172: Smaller Patch Panel
For a small site a smaller patch panel that does not require a relay rack may be used
This type attaches directly to the wall or a shelf as seen in the next slide

## Slide 173: Smaller Patch Panel

## Slide 174: Patch Panel in Ceiling

## Slide 175: UTP Wiring Schemes
The next step is to terminate the cable
As discussed before recall that you must decide what wiring scheme to use
There are two schemes
  568A
  568B

## Slide 176: Cable Management
Once the cable has been installed and terminated, it needs to be managed, because cable management keeps termination fields neat and orderly, and provides strain relief for the cable
Strain relief transfers the weight of the cable from the cable itself to some sort of supporting hardware

## Slide 177: Cable Management
Without strain relief, the weight of the cable will cause it to sag and eventually pull away from its termination
Cable ties are the most popular method of attaching cables to support hardware
These thin plastic strips are looped around a bundle of cables and cinched tight enough to support the cables

## Slide 178: Cable Management
Cable ties also make large bundles of cables more manageable and give the installation a neat appearance
But over-cinching of cable ties has the same effect as tight bends
The conductors of the outermost cables in the bundle tend to become flattened

## Slide 179: Cable Management
A proper cinch of a cable tie will allow the cables to slide easily back and forth within its loop
Staples are not recommended for Category 5 and above installations
Cable management can also be done by attaching plastic channels with or without covers to the relay rack as seen above

## Slide 180: Terminating in the Work Space
The next step is to terminate the cable in each work space area
There are two main ways to attach the jack used to terminate the cable in the work area
  Flush Mount
  Surface Mount

## Slide 181: Flush Mount Termination
The next set of photographs shows the parts required to do a flush mount termination in the work area and the steps involved
This is only one of many ways to do this

## Slide 182: PC Plugged Into Wall Plug

## Slide 183: Wall Plate in Office

## Slide 184: Wall Plate in Office

## Slide 185: Wall Box

## Slide 186: Hole for Wall Box

## Slide 187: Wall Box Mounted to Stud

## Slide 188: Wall Box Mounted to Stud

## Slide 189: Wire Run Up Wall in Office

## Slide 190: Fold in Plate Wall Box

## Slide 191: Jack
The wire is terminated into a jack of which there are many styles
Discussed next are two examples

## Slide 192: Jack

## Slide 193: Jack

## Slide 194: Jack

## Slide 195: Surface Mount Termination
The second main way to place the termination point in a work space is by using a box that mounts directly to the wall
This avoids the problem of cutting a exact size hole in the wall
In some cases this takes too long
In other cases the wall is not suitable for this type of cutting

## Slide 196: Surface Mount Box

## Slide 197: Raceway
The wire going to a surface mount box can be just dropped out of the ceiling as seen in the next slide
But do not do this, It looks awful
Instead use raceway as shown below

## Slide 198: Wire Dropped From Ceiling

## Slide 199: Raceway

## Slide 200: Raceway

## Slide 201: Switched Jacks
When you find you do not have enough ports in an area an easy way to add more is a switched jack
The one from 3Com looks like this
Power to this switch is through Poe
This might be a way to expand a cabling installation, without adding cable

## Slide 202: Switched Jacks

## Slide 203: Wall Plate
The box opening is covered with a plate
Which is attached by screws as shown

## Slide 204: Wall Plate

## Slide 205: Labeling
Finally the outlet is labeled to correspond to the other end

## Slide 206: Labeling

## Slide 207: Industrial Environments
Ethernet based networks have not been used on the factory floor due to an inability to predict and control latency
This lack of low latency is due to Ethernet not being a deterministic network
However with increases of speed to 100 Mbps and above latency values are now in the microsecond range, which is sufficient for factory floor operations

## Slide 208: Industrial Environments
In the office a latency of 5 seconds or 500 milliseconds does not matter
However milliseconds count on the shop floor
A lack of timing creates defects and compromises safety
2 to 5 mms is required for this

## Slide 209: Industrial Environments
The increasing interest in Ethernet is due to a desire to reduce cost
Common industrial network access methods such as Modbus, Profibus, ControlNet and DeviceNet are proprietary, and therefore expensive
Ethernet is a standard and much lower in cost

## Slide 210: Industrial Environments
To work in an industrial environment Ethernet equipment must be more robust for the harsher environment seen on the industrial floor
The ability to prioritize traffic is important as well

## Slide 211: Industrial Environments
STP is typically too slow for the shop floor
Rapid STP is better

## Slide 212: Industrial Ethernet
One of the primary differences in the equipment
Commonly this includes
  Harsh environment equipment
    Temperature from -40C to +70C
    95% non-condensing humidity
  Convection cooling
  Relay output signaling
  24 volt DC power

## Slide 213: Industrial Environments
Installing equipment on a plant floor produces special problems
Most of these are related to the environment found there

## Slide 214: Industrial Environments
The main problems are related to
  Dirt and dust
  Electrical noise
  Contaminants
  Temperature
  Moisture
  Vibration
  Crush

## Slide 215: Industrial Environments
In general the higher the data rate the more susceptible to noise a data channel is
Dirt and Dust
  This is always present in a shop environment
  The common RJ-45 connector will not keep this type of material out

## Slide 216: Industrial Environments
Electrical Noise
  This comes from the plant floor equipment
  In general this is produced as EMI – Electro Magnetic Interference by devices such as arc welders
  And RF – Radio Frequency
  It is especially important to separate data cables from other cables in their own raceway

## Slide 217: Industrial Environments
  These cables must be kept at least 1.5 to 3 inches from sources of interference, even in a raceway
  A balanced cable provides very good immunity to noise
  When balanced each consecutive half-twist of the cable is in the opposite direction in terms of which wire is on top of the twisted pair
  This helps to cancel out noise coupled on the pair

## Slide 218: Industrial Environments
  It is best to use a bonded cable where the pairs of wires are bonded to each other to keep this orientation
  STP or fiber optic cable must be used in extreme conditions

## Slide 219: Industrial Environments
Contaminants
  These come from the chemicals and fumes commonly used in industrial environments
  They will degrade components designed for the office environment
  For example oil causes the jacket to swell and lose its mechanical strength
  This will increase the chances that contamination will penetrate to the core

## Slide 220: Industrial Environments
Temperature
  High temperatures will change the DC resistance
  This in turn increases the attenuation
  Common inside UTP cable rate of attenuation will increase at a rate of 0.4% per degree Celsius above 20 degrees C, and at 60 degrees C the attenuation can increase by 16%

## Slide 221: Industrial Environments
Moisture
  This can be from ambient conditions
  It can also come from pressure washing of equipment on the shop floor
Vibration
  Office components do not have connectors designed for the high levels of vibration seen in industrial equipment in many cases

## Slide 222: Industrial Environments
Crush
  People walk on cables, vehicles drive over cables
  None of this is very good for the cable
  Install the cables in cable trays above the equipment or in extreme cases use metal or plastic conduit
Some of this information came from a study done by Rockwell Automation and Anixter

## Slide 223: Industrial Environments
Here is a summary table from a Belden webinar from July 2013 of these problems

## Slide 224: Industrial Environments

## Slide 225: Industrial Environments
Other than the cable, discussed below, the connector is the main problem in this type of environment
The standard RJ-45 connector will allow all of this crud in
A sealed connector works better
For example, this photograph from Siemon’s shows the effect of high moisture on a standard RJ-45 connector

## Slide 226: Industrial Environments

## Slide 227: Industrial Environments
To combat this, Siemons at least, recommends a more sealed connector, such as the Siemon Industrial MAX
This looks like

## Slide 228: Industrial Environments

## Slide 229: Industrial Environments

## Slide 230: Industrial Environments
Here’s what the Hubbell version looks like

## Slide 231: Industrial Environments

## Slide 232: Industrial Environments
The idea here is this style of connector will keep out most of the moisture and resist loosening from vibration
The TIA-1005 standard covers industrial environments
The thrust of this effort is to meet one of the IP – International Protection levels that have been defined by the IEC for connectors

## Slide 233: Industrial Environments
IP is also used to stand for Ingress Protection as these standards are primarily concerned with preventing the entry of things from the outside world
The IP rating will be used to indicate the degree of protection afforded by the device

## Slide 234: Industrial Environments
This will not only be connectors, but all of the other parts required for a complete cabling solution
For example a rating of IP67 would indicate by the first number the amount of protection provided to the users from hazardous parts inside the enclosure and the protection provided to the parts inside against ingress of solid objects

## Slide 235: Industrial Environments
The second number is the degree of protection from water entering the device
Here are the suggested ratings

## Slide 236: Industrial Environments

## Slide 237: Industrial Environments
There is some resistance to this effort to introduce Ethernet connectors to the plant floor
The traditional connector for these applications is the M12
Many users prefer to stay with some style of this connector

## Slide 238: Industrial Environments

## Slide 239: Industrial Environments

## Slide 240: Industrial Environments
In the same Belden webinar from July 2013 they pointed out the advantage of using bonded cable pairs inside the UTP cable to lessen noise problems

## Slide 241: Industrial Environments

## Slide 242: Industrial Environments
Good practice is to change components such as patch cables that are exposed on a scheduled basis just in case

## Slide 243: ScTP
ScTP – Screened Twisted Pair cable is sometimes used in manufacturing and industrial environments in the US
This cable was discussed previously

## Slide 244: Cabling Security
Security for the cabling system may be a consideration as well
Cables can be tapped physically or by sensing the EMI they put off
Conduit may be run throughout the building to help prevent this
However, this is quite expensive

## Slide 245: Cost of Installation
The cost of any cable installation will vary depending on the particular environment encountered
In general it takes, for initial installation of many cables at one time, the following times for each single cable installation, termination, and test
  Placement of 150 feet of cable – 30 minutes
  Work area termination – 15 minutes

## Slide 246: Cost of Installation
  Patch Panel termination – 30 minutes
  Labeling and testing – 15 minutes
  For a total of 90 minutes for a typical horizontal cable installation on average when many are done for a single job
Times and costs are higher when only a single cable is being installed
In this case
  Placement of 150 feet of cable – 60 minutes

## Slide 247: Cost of Installation
  Work area termination – 20 minutes
  Patch Panel termination – 30 minutes
  Labeling and testing – 15 minutes
  This totals 120 minutes for an added cable to an existing installation

## Slide 248: Putting the Project Out for Bid
If you decide that all of this is too much trouble, which it is, then you may want to hire someone who knows what they are doing to install the cable for you
A excellent way to do this is to have several companies bid on the job
The BICSI has a document on their web site which can be adapted for this purpose
It is quite comprehensive

## Slide 249: Putting the Project Out for Bid
Even if you do not plan to put a job out for bid, I recommend you read through it just for the information included in it concerning cabling

## Slide 250: Sources
Some of the photographs used are from the L-com catalog with their permission

## Slide 251: For More Information
Network Cabling
  Chris Clark
  ISBN 0072132337
Cabling: The Complete Guide to Network Wiring
  David Groth and Jim McBee
  ISBN 0782126456
The Cabling Handbook - 2nd Edition
  John R. Vacca
  ISBN 0130883174

## Slide 252: For More Information
The Telecommunications Industry Association
  http://www.tiaonline.org/index.cfm