## Slide 1: Terminating Fiber Optic Media
Last Update 2011.09.16
1.8.0

## Slide 2: Objectives
Learn how to terminate fiber optic media

## Slide 3: Handling Fiber Optic Media
Anytime you work with fiber optic cable it is important to keep everything clean
It is also important to protect yourself from injury from small pieces of fiber
These fiber pieces that are produced as a normal part of the termination process can get in your eyes or stick in your skin
They are difficult to remove

## Slide 4: Work Space
The proper work space for fiber optic cable is on top of a non-reflective black surface so any loose fiber pieces can be seen
Tweezers should be used to pick up any stray pieces, which are then placed in a container made for this purpose

## Slide 5: Keeping Yourself Safe
Whoever is working with the fiber should wear safety glasses
Do not rub your eyes or skin without washing your hands

## Slide 6: Keeping the Media Clean
It is critical that the ends of fiber optic cable be kept clean
Dirty connections are a common cause of link failures
According to Fluke 85% of link failures are due to contaminated ends

## Slide 7: Inspection
The best way to check for dirt is an inspection scope
For multimode fiber 200 times magnification is used
For single mode cable 400 time is required

## Slide 8: Inspection Scope

## Slide 9: Inspection Scope

## Slide 10: Inspection Scope

## Slide 11: Inspection Process

## Slide 12: Sources of Problems
The are two main sources of problems on fiber ends
  Contamination
    Dirt and Dust
    Finger Prints
    Cleaning Method Used
    Skin Oils and Cable Gels
  Damage
    Pitting
    Scratches

## Slide 13: Contamination
There are many sources of contamination that leads to dirt particles on connections
  Airborne dust and dirt
  Improper or insufficient cleaning of tools and materials
  Debris from poor quality components
  Dirt from the technicians hands
Here are some examples of common problems from Fluke and others

## Slide 14: Contamination
Even touching the end of a fiber will deposit excessive oil
Gel from used to pull cable will do the same thing
Dust caps do not necessarily help as they may transfer contamination

## Slide 15: Dust

## Slide 16: Dirt

## Slide 17: Finger Print

## Slide 18: Dirt

## Slide 19: Dust and Skin

## Slide 20: Dust and Skin

## Slide 21: Dust and Skin

## Slide 22: Dry Cleaned

## Slide 23: Too Much Solvent Cleaner

## Slide 24: Pitting
In some cases the amount of dirt is so great that scratches, pits, and chips can be seen in the fiber ends

## Slide 25: Scratches

## Slide 26: Scope Resolution
In general scopes have one of three resolutions
  Low – 60X
    This does not show much detail, but it has a wide field of view
  Medium – 200X
    This will show dirt, oils, dust, and lint
  High – 400X
    This level will show pits and scratches as well

## Slide 27: Scope Resolution
In the field the 200X is the most widely used

## Slide 28: Cleaning
The solution to this problem is proper cleaning
This means the use of optical grade materials to do the cleaning
Cleaning can be done using dry or wet methods

## Slide 29: Best Practice When Cleaning
As discussed below there are many suggested methods for cleaning fiber
To cut to the chase here is what Fluke says is the best way to do this regardless of whether it is a plug or jack

## Slide 30: Best Practice When Cleaning
  Dab the contaminated end-face with a solvent-dampened wipe or swab
  The solvent dissolves and removes contaminants that have dried and firmly affixed to the end-face without producing a static charge that can attract dust from the air
  It also evaporates quickly, making it preferable to isopropyl alcohol which takes much longer to disappear and can leave a staining residue in the process

## Slide 31: Best Practice When Cleaning
  Rub the fiber end-face perpendicularly against a dry wipe several times
  Re-inspect the fiber end-face with an optical microscope to ensure that all the debris has been removed

## Slide 32: Dry Cleaning
Dry cleaning is very common
However it can lead to static charges on the ends of the connectors
These charges then attract dust

## Slide 33: Wet Cleaning
Although an extra step, wet cleaning is more effective
Isopropyl alcohol at 99 percent is commonly used for this purpose
While effective alcohol must be allowed time to dry, since alcohol will absorb water from the air
There are solutions designed for fiber optic cable that are a better choice

## Slide 34: Cleaning Cable Ends
Let’s look at some common methods used to clean fiber optic media as provided by Fluke
Using Fluke Networks Fiber Optic Cleaning Card
  Peel cover from an unused “N”– shaped cleaning zone
  Apply a minimal amount of solvent from the Solvent Pen to the first corner of the “N”

## Slide 35: Cleaning Cable Ends
  Avoid isopropyl alcohol
  Place the end-face perpendicular to the card in the first corner of the unused “N”
  Swipe through the “N” shape using gentle pressure moving from wet to dry
  Always check the end-face with a fiber microscope before insertion
  If necessary, repeat the cleaning process from step #1 using another unused “N”
  Never swipe over the same area twice

## Slide 36: Cleaning Cards

## Slide 37: Cleaning Cable Ends
Using Fluke Networks’ Fiber Optic Cleaning Cube
  Pull out a clean wipe and lay it over the foam platen
  For best results, apply a minimal amount of solvent from the Solvent Pen
  A 1 cm diameter spot is sufficient
  Avoid isopropyl alcohol

## Slide 38: Cleaning Cable Ends
  Place the end-face perpendicular to the cube in the wet spot
  Swipe the end-face from the wet spot into a dry area using gentle pressure
  Always check the end-face with a fiber microscope before insertion
  If necessary, repeat the cleaning process on a clean portion of the wipe
  Each wipe can clean up to four end-faces. Never swipe over the same area twice

## Slide 39: Cleaning Cube

## Slide 40: Cleaning Cable Ends
Using Fluke Networks’ Fiber Optic Swabs
  Select the swab with the correct diameter to fit inside the port to be cleaned. 2.5 mm Fiber Optic Swabs fit SC, ST, and all other 2.5 mm diameter ports. 1.25 mm Fiber Optic Swabs fit LC and MU ports
  Using the Fiber Optic Cleaning Cube or Card, apply some solvent from the Solvent Pen to a wipe
  Avoid isopropyl alcohol

## Slide 41: Cleaning Cable Ends
  Touch the swab to the wet spot on the wipe for 3 seconds to draw a minimal amount of solvent
  Touching the swab directly to the Solvent Pen will likely result in excess solvent
  Insert the damp swab into the port and turn several times, applying gentle pressure

## Slide 42: Cleaning Cable Ends
  Follow the damp swab with a dry one, using the same procedure to remove any remaining solvent from the end-face and alignment sleeve
  Always check the end-face with a fiber microscope before insertion
  If necessary, repeat the cleaning process with fresh swabs

## Slide 43: Cleaning Swabs

## Slide 44: Cleaning Swabs

## Slide 45: Area to Clean
It is important to clean not only the core area of the fiber end, but also the cladding area
In this photograph the core is the white dot the cladding is the dark circle

## Slide 46: Area to Clean

## Slide 47: Area to Clean
Failing to clean the cladding area as well as inside the connector itself will allow the debris there to migrate to the core, thus blocking the light based signal
Clean both the patch cord ends as well as the bulkhead connectors such as these

## Slide 48: Area to Clean

## Slide 49: Field Termination Methods
There are three basic termination methods that can be used in the field
The selection of which one to use is best decided by balancing the
  Cost of the method
  The loss the method creates
  The ease of keeping the ends clean

## Slide 50: Field Termination Methods
The three common field termination methods are
  MPO
  Factory terminated pigtails
  Field termination
Lets look at each of these

## Slide 51: MPO
An MPO connector is a three part system of
  Cassette Connector at Originating End
  Preterminated Cabling
  Cassette Connector at Other End
For example

## Slide 52: MPO Cassette

## Slide 53: MPO Cable

## Slide 54: MPO
Notice that the cassette is ready to be placed in a rack
The end facing out is ready to accept a fiber optic cable patch cord
The end facing the back is ready to accept a preterminated cable that will run from this MDF or IDF to the other end of the connection

## Slide 55: MPO
Further as the photograph of the MPO cable shows these cables are preterminated
They merely need to be installed in the building
This means no termination is required in the field

## Slide 56: MPO
The disadvantage to this method is
  Higher cost
  Need to accurately measure the length of the cable
  Higher loss

## Slide 57: Factory Terminated Pigtails
This method is similar to the MPO method except the back facing connection of the box mounted in the rack is non preterminated
A standard fiber optic cable is installed in the building, then the cable attached to the rack mounted patch panel using one of the methods discussed below

## Slide 58: Factory Terminated Pigtails
This method has advantages and disadvantages
  Cost is lower
  Loss is less
  Labor cost is higher
  Greater installer expertise is required

## Slide 59: Field Termination
When using this method everything is done in the field
  Connectors are terminated at both ends
  The connectors are installed in a patch panel
  The cable is installed
  The cable ends are attached to the connectors

## Slide 60: Field Termination
This method as well as advantages and disadvantages such as
  Lowest cost for parts
  Lowest loss
  Highest labor cost
  Greatest installation expertise required

## Slide 61: Attaching Connectors
There are several ways to attach connectors to fiber optic cable, such as
  Polish
    Oven cured epoxy
    UV cured epoxy
    Anaerobic epoxy
  No Polish
    Clamp

## Slide 62: Attaching Connectors
Here is a summary from Cabling Installation and Maintenance from January 2011

## Slide 63: Attaching Connectors

## Slide 64: Basic Termination Steps
Regardless of the method used there are several basic steps in fiber optic cable termination
  Strip the covers off the fiber
  Secure the fiber to the connector
  Cleave the fiber
  Polish the end in some cases
  Inspect the end

## Slide 65: Oven Cured Epoxy
Oven cured epoxy makes the best connection
But it is the most trouble to use
This process requires mixing the resin and hardener in the correct proportions
All of it must be used before it sets up
Any that is not used, must be thrown out

## Slide 66: Oven Cured Epoxy
This method is best suited for making a number of similar connections
Once the glue is applied to the connection, it is placed in an oven for around 45 minutes to set
Then the connector is put in a tray to cool

## Slide 67: Oven Cured Epoxy

## Slide 68: Oven Cured Epoxy

## Slide 69: UV Epoxy
With the UV epoxy an ultraviolet lamp is used to cure the epoxy in about 1 minute

## Slide 70: Anaerobic Epoxy
No tools are required for anaerobic epoxy
One part is applied to the fiber
The other part to the ferrule
When the two are joined the two solutions interact to form the bond
This takes about 10 seconds
The drawback to this method is a weaker joint

## Slide 71: Tools
Several types of tools are used to terminate fiber optic cable
These are for
  Cutting
  Cleaning
  Marking
  Polishing

## Slide 72: Tools for Cutting
Shears
  For removing the strength member
Stripper
  For removing the outer cover
Stripper
  For removing the fiber buffer
Scribe
  To cut the fiber inserted in the connector

## Slide 73: Tools for Cleaning
Cleaning solution
  To carry away contaminants
Lint free wipes
  To remove the cleaning solution

## Slide 74: Tools for Marking
Fiber marker
  To mark where to remove the covers

## Slide 75: Tools for Polishing
Glass plate
  To support the soft pad
Soft pad
  So the abrasive can properly contact the fiber
Abrasives
  To grind down the end of the fiber
Puck
  To hold the connector while polishing

## Slide 76: Basic Procedure for Connector
The basic process for attaching a connector is
  Cut the cable longer than required by a couple of inches
  Slide any parts onto the cable that cannot be added later such as the strain relief boot
  Strip off the outer cover
  Mark the cable at the points required for the connector preparation

## Slide 77: Basic Procedure for Connector
  Remove the cable jacket
  Cut the strength member off flush to the remaining jacket
  Strip off the buffer in small sections so as to not break the fiber
  Clean the fiber
  Clean the connector
  Dry fit the connector
  Apply the glue based on the type used

## Slide 78: Remove the Outer Cover

## Slide 79: Remove the Outer Cover

## Slide 80: Remove the Strength Member

## Slide 81: Remove Buffer Around Fiber

## Slide 82: Remove Buffer Around Fiber

## Slide 83: Polishing
For polish type connectors the exact procedure will vary based on the specific connector used
Basically the end of the ferrule is already of the desired end face dimension
The purpose in polishing is to form the fiber end to the shape and size of the ferrule’s end face

## Slide 84: Polishing
A puck is used to hold the connector with the fiber installed in the correct orientation

## Slide 85: Polishing Procedure
In general the method to use to polish is
  Be sure the glue is dry
  Scribe the fiber at the base of the glue bead at the end of the connector
  Smooth the resulting nub with a piece of 5 micron film by gently rubbing it
  Place the glass plate under the soft pad
  Place the 5 micron abrasive on the soft pad

## Slide 86: Polishing Procedure
  Place the connector in the puck
  Place the puck on the film
  Begin polishing using a figure 8 pattern
  Make about 20 patterns
  Clean the end
  Change to the 0.3 micron film
  Using the puck and the figure 8 pattern continue until the end is smooth

## Slide 87: Polishing Procedure

## Slide 88: Fiber End Face Finishes
There are several different end face finishes that can be done
PC - Physical Contact finish is the most common
Other include UPC – Ultra Physical Contact and APC – Angled Physical Contact

## Slide 89: Fiber End Face Finishes
Each of these of increasing reduction of back scatter, in other words loss at the connections
For example

## Slide 90: Fiber End Face Finishes

## Slide 91: Scribe

## Slide 92: Scribe

## Slide 93: Polish Off the Pad

## Slide 94: Polish On the Pad

## Slide 95: Polish On the Pad

## Slide 96: Polish On the Pad

## Slide 97: No Polish Procedure
Corning has a commonly used no polish connector called the UniCam
Let’s let them explain how this works and the procedure used to do this

## Slide 98: Clamp On Connector Operation
  The patented UniCam connector incorporates a mini-pigtail housed in a connector body
  There is a fiber stub bonded into the ferrule in the factory, where the end-face of the ferrule is polished to a PC, UPC, or APC finish
  The other end of the fiber is cleaved and fully protected inside the connector
  The field fiber is cleaved and inserted into the connector until it makes positive contact with the fiber stub

## Slide 99: Clamp On Connector Operation
  A simple rotating cam actuation process completes the connector with no epoxy or polishing required
  After strain relieving the fiber to the connector, it is ready to be mated to another connector inside an adapter
  The primary advantage of a UniCam connector, when compared to other field-installable connector methods, is the time savings

## Slide 100: Clamp On Connector Operation
  Because no epoxy or polishing is required in the field, a UniCam can be installed very quickly, leading to labor cost savings and the ability to increase the volume of installations
  This provides installer, contractors, and end users the ability to complete installations more quickly, bringing critical systems on line, and moving on to the next revenue-generating opportunity

## Slide 101: Clamp On Connector Operation
  An important advantage of the UniCam connector design over other no-cure connectors is that the fiber is fully protected from the environment
  The epoxy process and polishing process in the factory are carefully performed to make certain the UniCam connector will last virtually the entire life of the network

## Slide 102: Clamp On Connector Operation
  Another significant advantage of the UniCam connector can be attained when used for installations at the desk outlet or other areas with limited physical space
  The only tools required are a stripper, a cleaver, the installation tool, and an alcohol pad

## Slide 103: Clamp On Connector Procedure
The basic steps to attach a fiber optic cable to a no polish, clamp on connector are
  Open the tool
  Open the connector
  Place the connector in the tool
  Slide the strain relief boot over the fiber optic cable

## Slide 104: Clamp On Connector Procedure
  Strip 1.5 inches of the buffer off the fiber to expose the fiber itself
  Clean the fiber
  Cleave the fiber
  Insert the fiber into the connector
  Close the tool
  Seat the clamp
  Install the rest of the hardware

## Slide 105: UniCam Buffer Stripping Tool

## Slide 106: UniCam Cleaver

## Slide 107: The UniCam Tool

## Slide 108: Inspect the Fiber End
Using the appropriate power scope examine the fiber end using the guidelines seen in the photographs above and these examples from the Woodard and Husson book

## Slide 109: Inspect the Fiber End

## Slide 110: Inspect the Fiber End

## Slide 111: Inspect the Fiber End

## Slide 112: Inspect the Fiber End

## Slide 113: Inspect the Fiber End

## Slide 114: Inspect the Fiber End

## Slide 115: Splicing Fiber Optic Cable
There are two ways to connect one piece of fiber optic cable to another
These are
  Fusion
  Mechanical
Without extensive training and expensive tools the only splicing you are likely to do is a mechanical splice

## Slide 116: Fusion Splice
A fusion splice is a junction of two or more optical fibers that have been melted together
This is accomplished with a machine that performs two basic functions
  Aligning of the fibers
  Melting them together
    Typically using an electric arc

## Slide 117: Fusion Splice
A machine, called a fusion splicer is used for this
A properly made fusion splice results in a continuous length of material with minimal discontinuities at the splice

## Slide 118: Fusion Splicer

## Slide 119: Mechanical Splice
A mechanical splice is an optical junction of two or more optical fibers that are aligned and held in place by a self-contained assembly - usually the size of a large carpenter's nail
The fibers aren't permanently joined, just precisely held together so that light can pass from one to another

## Slide 120: Mechanical Splice

## Slide 121: Mechanical Splice

## Slide 122: Which Splice to Use
Several considerations determine which splice method to use
The first is the economics
  Tools for a mechanical splice cost around $1,500
  The consumable of the mechanical splice is about $12 in 2011

## Slide 123: Which Splice to Use
  Fusion splices, on the other hand, require a large capital investment up front to purchase a fusion splicing machine
  After that, the only consumable cost is in the protective device, which is generally $1 or less each

## Slide 124: Which Splice to Use
Second is performance
  Fusion splices typically provide lower loss and reflect less light than mechanical splices
  For all intents and purposes, the splice point is transparent in a fusion splice
For most LAN applications, splice loss and reflections are minor concerns
However, splice loss must be minimized for WANs

## Slide 125: Fusion Splice Procedure
Fusion splicing consists of four basic steps, regardless of how sophisticated a machine is
  Prepare the fiber
  Cleave the fiber
  Fuse the fiber
  Protect the fiber

## Slide 126: Fusion Splice Procedure
Preparing the fiber is accomplished by stripping away all the protective coatings, jackets, tubes, until all that is left is the bare fiber
The main concern is cleanliness
A clean fiber is essential for the all important cleaving step
Cleaving is the cutting of the fiber

## Slide 127: Fusion Splice Procedure
Cleaving the fiber properly is the key to successful splicing
It is virtually impossible to make a good fusion splice with a poor cleave
The idea here is to have a mirror-smooth, perpendicular fiber end

## Slide 128: Fusion Splice Procedure
A common misconception is that the cleaver actually cuts the fiber in half
Actually, the process is the same as cutting a window pane to size, only on a much finer scale
The cleaver first nicks the fiber, and then pulls or flexes it to cause a clean break

## Slide 129: Fusion Splice Procedure
A high degree of precision is required, which is why good cleavers can cost $1,000 to $4,000
Fusing comes next
It consists of two steps
  Aligning
  Heating
Protecting the completed splice is the final step

## Slide 130: Fusion Splice Procedure
A fusion splice will typically have a tensile strength between 0.5 and 1.5 lbs
A good splice will not break during normal handling, but it must be protected from bending and tensile forces
Fusion splicing times can vary drastically depending on the end result required
Basic machines can do simple splices in 10-15 seconds

## Slide 131: Fusion Splice Procedure
The most precise machines on the market can take one minute or longer per splice
Why the difference
The precise machines spend much more time prior to the splice analyzing and precisely aligning the fibers

## Slide 132: Fusion Splice Procedure
The basic machines make few assumptions and splice with a quick alignment process, without the extra analysis
Fusion splicers cost anywhere from $7,000 to $12,000 in 2011
The difference depends entirely on the special features and the accuracy of the machine

## Slide 133: Fusion Splice Procedure

## Slide 134: Mechanical Splice Procedure
Mechanical splicing requires the same four steps as fusion splicing, with a slight modification in step three
  Prepare the fiber
  Cleave the fiber
  Mechanically join the fiber
    Using no heat
  Protect the fiber

## Slide 135: Mechanical Splice Procedure
The basic procedure for performing a mechanical splice is
  Strip about 1 to 2 inches of the plastic coating from the fiber ends to be spliced using a stripping tool
  Place the splice in the assembly tool
  Clean the bare glass by pulling it through a alcohol wipe made for fiber optic cable
  Cleave the fiber to the length specified for the splice device or tool

## Slide 136: Mechanical Splice Procedure
  This is usually 12 to 14 mm
  Usually there is a gauge on the assembly tool
  Insert one side of the fiber into the holder on the tool
  Insert the fiber end into the splice
  Push until resistance is met
  The fiber should have a slight bow
  Insert the other fiber into the splice
  Push second fiber until it moves the first fiber

## Slide 137: Mechanical Splice Procedure
  Push the first fiber back in to equalize the bows
  Use the assembly tool to attach the splice to the two pieces of fiber
  Remove the completed splice
  If called for, cover the splice with a provided protective cover

## Slide 138: Mechanical Splice Procedure
Preparing the fiber is done the same way as for fusion splicing
Cleaving the fiber is done the same way as for fusion splicing, but less precision is required
There are a number of technical reasons why mechanical splices are more forgiving of poor cleaves than fusion splices

## Slide 139: Mechanical Splice Procedure
The main reason is that there is an index matching gel in the center of the mechanical splice that helps couple the light from one fiber to the other fiber
A typical cleaver for mechanical splicing will cost from $200 to $1,000
The fibers are brought together and held in place by the mechanical splice
No heating of the fibers takes place

## Slide 140: Mechanical Splice Procedure
The completed mechanical splice provides its own protection for the splice
Losses of 0.02 to 0.10 dB are typical for this type of connection

## Slide 141: Sources
Several points are from an article from the BICSI News November/December 2007
Some procedures and photographs from Fiber Optics by Bill Woodard and Emile B. Husson
The UniCam information is from Corning

## Slide 142: Lab
Review the videos under the Lab link for this course