## Slide 1: Data Center Design Last Update 2012.10.24 1.1.0

## Slide 2: Objectives
To see how the basic design principles should be adjusted for a data center

## Slide 3: What is a Data Center
A data center is a place where the data stores and other controlled shared resources are placed
The trend on where the data center should be goes back and forth from centralization to decentralization

## Slide 4: What is a Data Center
The argument, to which there is no answer, is between lower cost through centralization as desired by IT and control of resources through decentralization that is desired by the business units
One side will win the battle, then the other side

## Slide 5: What is a Data Center
This back and forth cycles on about a five year basis because there are compelling advantages on each side

## Slide 6: Mainframe Data Center
Data centers began with the mainframe era beginning in the 1950s
In the early days of computer networks the computers were too expensive for everyone to have
Therefore a single computer was shared by many users
This single large shared computer was called a mainframe

## Slide 7: Mainframe Data Center
These original data centers were centralized in one location
Users requested information or asked for jobs to be done by the mainframe computer by interacting with it through a terminal for real time processing or by submitting a job for processing using punch cards

## Slide 8: Mainframe Data Center
This job processing could be immediate or overnight
This type of data center still exists although the method of interaction has moved from terminals and punch cards to PCs
The data center format is still used because of its processing power and high availability

## Slide 9: Mainframe Data Center

## Slide 10: Client Server Data Center
The next iteration of the data center was the client/server model
Applications were installed on servers in a data center
These applications were accessed by users with client software running on their PCs

## Slide 11: Client Server Data Center
In many cases these application servers were distributed rather than centralized because of high cost of WAN links and application performance issues
These distributed servers could be individual computers the size of PCs with more robust hardware or mid range size computers that were between mainframes and PCs in size and computing power

## Slide 12: Client Server Data Center

## Slide 13: Web Based Data Center
In the current model for the data center the servers are once again centralized as the cost of WAN links has dropped while their speed has increased
Further the number of physical servers is being reduced as single servers are being moved to blade servers running virtual machines

## Slide 14: Web Based Data Center
The driving force here as always is to reduce the cost

## Slide 15: Web Based Data Center

## Slide 16: Virtualization in the Data Center
Virtualization in the data center is moving from just virtual servers to include
  Server virtualization
  Storage virtualization
  Network virtualization

## Slide 17: Unified Fabric
The physical infrastructure used in the data center has included Ethernet based LANs, Fibre Channel based SANs, and other proprietary connection types
The trend is toward using Ethernet as the single infrastructure with the storage data running on FCoE – Fibre Channel Over Ethernet

## Slide 18: Topology
Here is the suggested topology as illustrated in the Official Cert Guide for the CCDA test by Bruno and Jordon from Cisco Press

## Slide 19: Topology

## Slide 20: Topology
Here is how they describe this data center topology
  At the top layer, we have virtual machines which are software entities that have hardware level abstraction capable of running a guest OS on top of a resource scheduler also known as a hypervisor
  Within the unified computing resources, the service profile defines the identity of the server

## Slide 21: Topology
  The identity contains many items such as memory, CPU, network cards, storage information, and boot image
  10 Gigabit Ethernet, FCoE, and Fibre Channel technologies provide the unified fabric and is supported on the Cisco Nexus 5000

## Slide 22: Topology
  FCoE is one of the key technologies that allow native Fibre Channel frames to be used on 10G Ethernet networks
  Virtualization technologies such as VLANs and VSANs provide for virtualized LAN and SAN connectivity by logically segmenting multiple LANs and SANs on the same physical equipment
  Each VLAN and VSAN operates independently from one another

## Slide 23: Topology
  At the lowest layer, we have virtualized hardware where storage devices can be virtualized into storage pools and network devices are virtualized using virtual device contexts (VDC)

## Slide 24: Layout
A typical data center layout is shown in this slide by Commscope from an October 2012 webinar

## Slide 25: Layout

## Slide 26: Problem Areas
As data center are centralized issues arise such as
  Physical rack space
  Electrical power required
  Equipment cooling
  Limits to scale
  Security
  Virtualization support
  Management effort required

## Slide 27: Problem Areas
Here is what Bruno and Jordan say on these issues
  Server growth is consistently rising which is requiring more power, which is driving the need for energy efficiency for most data center server deployments
  Although rack servers are low cost and provide high performance, unfortunately they take up space and consume a lot of energy to operate

## Slide 28: Problem Areas
  Because both rack space and power cost money, efficiency gains need to be considered in these areas
  Blade servers provide similar computing power when compared to rack mount servers, but require less space, power, and cabling
  The chassis in most blade servers allows for shared power, Ethernet LAN, and Fibre Channel SAN connections, which reduce the number of cables needed

## Slide 29: Problem Areas
  With both rack-mounted servers and blade servers, server virtualization software provides for better utilization of hardware resources, which requires less physical hardware to deploy servers, which in turn increases efficiency
  Server virtualization also enables server scalability because more rack and cabinet space is available to deploy new ESX hosts running additional virtual machines

## Slide 30: Facility Planning
When planning the physical facility consideration must be given to
  Floor space needed
  How much load the raised floor can support
  Electrical power required
  Cooling capacity required
  The cabling that will be needed and how to manage it
For example

## Slide 31: Raised Floor

## Slide 32: Raised Floor

## Slide 33: Raised Floor

## Slide 34: Raised Floor Layout

## Slide 35: Raised Floor v Overhead Rack
Over the last few years opinion has coalesced around the idea that power cables should go under the raised floor and the data cables overhead in basket racks such as these

## Slide 36: Overhead Cable Racks

## Slide 37: Facility Planning
The environmental conditions in the data center is determined by the equipment as certain operating temperatures and humidity levels need to be maintained in the data center
The physical security of the data center must be planned from the beginning

## Slide 38: Facility Planning
Here is how Bruno and Jordan summarizes this

## Slide 39: Facility Planning

## Slide 40: Floor Space
The floor space needed is determined by
  The number of servers, amount of storage equipment, and networking equipment that will be needed
  The space needed for non-infrastructure areas such as
    Shipping and receiving
    Server and network staging
    Storage rooms, break rooms, and bath rooms
    Employee office space

## Slide 41: Equipment
As the authors state the equipment used will guide much of this as we consider
  Weight of the rack and equipment
  Heat expelled from equipment
  Amount and type of power needed
  Automatic transfer switch for equipment that has single power supplies
  Uninterruptible power supplies (UPS)
  Redundant power distribution units (PDU)

## Slide 42: Electrical Power
Several factors determine how much electrical power will be required including

## Slide 43: Electrical Power

## Slide 44: Electrical Power
Redundant power supplies are needed in the form of dual electrical supplies to the equipment
UPS based battery backup for short term power
Generator based backup for longer term power

## Slide 45: Cooling
Bruno and Jordan point out these considerations when designing the cooling system
  Cooling is used to control the temperature and humidity of the devices, and it is applied to zones, racks, or individual devices
  Environmental conditions need to be considered and measured by using probes to measure temperature changes, hot spots, and relative humidity

## Slide 46: Cooling
  A major issue with high-density computing is overheating
  There are more hot spots, and therefore more heat overall is produced
  The increase in heat and humidity threatens equipment life spans
  Computing power and memory requirements demand more power and thus generate more heat output

## Slide 47: Cooling
  Space-saving servers increase the server density possible in a rack, but keep in mind that density = heat
  It might not be a big deal for one chassis at 3 kilowatt (kW), but with five or six servers per rack, the heat output increases to 20 kW
  In addition, humidity levels can affect static electricity in the data center

## Slide 48: Cooling
  So, it is recommended that relative humidity level be in the range of 40 percent to 55 percent
  High levels of static electricity can cause damage to data center equipment
  Proper airflow is required to reduce the amount of heat generated by the high-density equipment

## Slide 49: Cooling
  Sufficient cooling equipment must be available to produce acceptable temperatures within the data center
  The cabinets and racks should be arranged in the data center with an alternating pattern of “cold” and “hot” aisles

## Slide 50: Cooling
  The cold aisle should have equipment arranged face to face, and the hot aisle should have equipment arranged back to back. In the cold aisle, there should be perforated floor tiles drawing cold air from the floor into the face of the equipment
  This cold air passes through the equipment and flushes out the back into the hot aisle

## Slide 51: Cooling
  The hot aisle does not have any perforated tiles, and this design prevents the hot air from mixing with the cold air
For example

## Slide 52: Air Flow Options

## Slide 53: Air Flow Options

## Slide 54: Cabling
Data center cabling is migrating from everything under the floor to moving the data cabling to overhead wireframe tracks
This helps air flow under the floor as well as making it easier to run and check data cables

## Slide 55: More on This
The presentation on Equipment Installation has much more detail on the facility issues briefly discussed here

## Slide 56: Design Layers
The data center follows the traditional three layer model

## Slide 57: Design Layers

## Slide 58: Virtualization
Virtualization is widely used in data centers for these reasons

## Slide 59: Virtualization

## Slide 60: Virtualization
Areas that can be virtualized include
  Servers
  Network
  Storage

## Slide 61: Standards
The TIA-942 standard along with the other structured cabling standards provide a guide to the setup of a data center

## Slide 62: Design Specifications
The standard calls for these specifications for the telecommunications room or closet
  This room should only be used for telecommunications functions
  Equipment not related to telecommunications shall not be installed, pass through or enter the telecommunications room
  Multiple closets on the same floor shall be interconnected by a minimum of one 78mm conduit, or equivalent pathway

## Slide 63: Design Specifications
  Minimum one closet per floor to house telecommunications equipment and cable terminations and associated cross-connect cable and wire
  Located near the center of the area being served.
  Horizontal pathways shall terminate in the telecommunications room on the same floor as the area served

## Slide 64: Design Specifications
  One wall should have 20mm (0.75 in.) A-C plywood 2.4m (8 ft.) high
  Lighting shall be a minimum of 500 lx (50 foot candles) at 1m (3 ft.) above finished floor (AFF)
  False ceilings shall not be provided
  Minimum door size 910mm (36 in.) wide and 2000mm (80 in.) high without sill, hinged to open outwards, or slide side-to-side or removable, and fitted with a lock

## Slide 65: Design Specifications
  Minimum of two dedicated 120V nominal non-switched duplex electrical outlet receptacles or equivalent, each on separate branch circuits
  Additional convenience duplex outlets placed at 1.8m (6 ft.) intervals around perimeter, 150mm (6 in.) above floor
  Access to the telecommunications grounding system as specified by ANSI-J-STD-607-A

## Slide 66: Design Specifications
  HVAC requirements to maintain temperature the same as adjacent office area
  A positive pressure shall be maintained with a minimum of one air change per hour or per code

## Slide 67: Design Specifications